## Valves export (1)
Technical informations | #1 |  | #2 | Primary product | [26 empty] | Secondary product | [21 empty] | Selection mode
|  |  |  | Product | [13 empty] | Technical informations | [9 empty] | Article N° | Local Art. Nr. | Qty | Product | [14 empty] | Technical informations |  |  |  | Article N° | Local Art. Nr. | Qty
|  |  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Location | Kvs | Qnom | Cable length to remote temp. sensor | Power Supply | Input | Output signal | Flow | Power/DT | Dp | Control mode | Dpl | Dp min. | Dp max. | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [9 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
[31 empty] | TA-Slider 160 Fail-safe R24 (2m HF) | Max force : 160 N | Actuating time : 10 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | : 0(2)-10 V | Relay 24V | Fail-safe type : Electronic | Fail-safe position : Configurable | [9 empty] | 322224-10715 |  | 1 | Direct selection
[31 empty] | TA-Slider 160 CO (5m) | Max force : 160 N | Actuating time : 10 s/mm | IP auto(man.) : 54 | 24 VAC | 0(2)-10 V | : 0(2)-10 V | Relay change-over | Fail-safe type : No | Default return position : None | [9 empty] | 322224-10513 |  | 1 | Direct selection
| BCV failsafe no |  |  | TBV-CM 15NF | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 24994 Pa |  |  |  |  | pos. 10* |  |  | 52144-115 |  | 1 | TA-Slider 160 Plus (2m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | Relay 220V | Fail-safe type : No | Default return position : None | [9 empty] | 322224-10212 |  | 1 | Individual selection
| BCV failsafe electro |  |  | TBV-CM 20NF | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 10000 Pa |  |  |  |  | pos. 8.25 |  |  | 52144-120 |  | 1 | TA-Slider 160 Fail-safe R24 (1m HF) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | Relay 24V | Fail-safe type : Electronic | Fail-safe position : Configurable | [9 empty] | 322224-10714 |  | 1 | Individual selection
| Pibcv failsafe no |  |  | TA-Fusion-P 32 | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00017 m3/s |  |  |  |  | 12000 Pa |  |  |  |  | *****-******(deleted) |  | 1 | TA-Slider 750 Plus (HV) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 115 VAC; 230 VAC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | Relay 220V | Fail-safe type : No | Default return position : None | [9 empty] | 322226-40219 |  | 1 | Individual selection
| pibcv failsafe electronic |  |  | TA-Fusion-P 32 | Ametal(tm) |  | Thread male | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00017 m3/s |  |  |  |  | 12000 Pa |  |  |  |  | *****-******(deleted) |  | 1 | TA-Slider 750 Fail-safe Plus (HV) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 115 VAC; 230 VAC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | Relay 220V | Fail-safe type : Electronic | Fail-safe position : Configurable | [9 empty] | 322226-40319 |  | 1 | Individual selection
| pibcv failsafe spring return |  |  | TA-Fusion-P 32 | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00017 m3/s |  |  |  |  | 12000 Pa |  |  |  |  | *****-******(deleted) |  | 1 | TA-MC 100FSE/24 | Close-off Dp : 800000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | No relay | Fail-safe type : Spring return | Fail-safe position : Extending | [9 empty] | *****-***(deleted) |  | 1 | Individual selection
| CV failsafe no |  |  | CV 206 GG DN65 | Cast iron | Kvs = 50 | Flange | Standard |  | PN6; -10/150 °C | [7 empty] | 0.0042 m3/s |  | 8892 Pa |  |  |  |  | - |  |  | 60215-165 |  | 1 | TA-Slider 750 Plus Modbus/RTU (HV) | Close-off Dp : 118750 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 115 VAC; 230 VAC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA; Modbus RTU | 0(2)-10 V; 0(4)-20 mA | Relay 220V | Fail-safe type : No | Default return position : None | [9 empty] | 322226-42219 |  | 1 | Individual selection
| Cv failsafe electro |  |  | CV 216 GG DN65 | Cast iron | Kvs = 63 | Flange | Standard |  | PN16; -10/150 °C | [7 empty] | 0.0042 m3/s |  | 5601 Pa |  |  |  |  | - |  |  | 60235-265 |  | 1 | TA-Slider 750 Fail-safe Plus (HV) | Close-off Dp : 118750 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 115 VAC; 230 VAC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | Relay 220V | Fail-safe type : Electronic | Fail-safe position : Configurable | [9 empty] | 322226-40319 |  | 1 | Individual selection
| Cv failsafe spring return |  |  | CV 216 GG DN65 | Cast iron | Kvs = 63 | Flange | Standard |  | PN16; -10/150 °C | [7 empty] | 0.0042 m3/s |  | 5601 Pa |  |  |  |  | - |  |  | 60235-265 |  | 1 | TA-MC 100FSR/230 | Close-off Dp : 150000 Pa | Actuating time : 180 s | IP auto(man.) : 54 | 230 VAC | 3-point | 0-10 V | No relay | Fail-safe type : Spring return | Fail-safe position : Retracting | [9 empty] | *****-***(deleted) |  | 1 | Individual selection
|  |  |  | TBV-CM 20NF | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00017 m3/s |  | 10000 Pa |  |  |  |  | pos. 9 |  |  | 52144-120 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail-safe type : No | Default return position : None | [9 empty] | 322224-10111 |  | 1 | Individual selection
|  |  |  | TBV-CM 20NF | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00017 m3/s |  | 10000 Pa |  |  |  |  | pos. 9 |  |  | 52144-120 |  | 1 | TA-Slider 160 Fail-safe I/O (1m HF) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | No relay | Fail-safe type : Electronic | Fail-safe position : Configurable | [9 empty] | 322224-10614 |  | 1 | Individual selection
|  |  |  | TA-Fusion-P 32 | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  |  |  |  | 12198 Pa |  | 0.31 turns |  |  | *****-******(deleted) |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail-safe type : No | Default return position : None | [9 empty] | 322226-10110 |  | 1 | Individual selection
|  |  |  | TA-Fusion-P 32 | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  |  |  |  | 12198 Pa |  | 0.31 turns |  |  | *****-******(deleted) |  | 1 | TA-MC 100FSE/24 | Close-off Dp : 800000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | No relay | Fail-safe type : Spring return | Fail-safe position : Extending | [9 empty] | *****-***(deleted) |  | 1 | Individual selection
| Dpcbcv failsafe no |  |  | TA-Compact-DP 20 |  | 20 (3/4") | Thread male | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00011 m3/s |  |  |  |  | 15522 Pa |  | pos. 2.75 | 20522 Pa |  | 52164-220 |  | 1 | TA-Slider 160 I/O (1m HF) | Close-off Dp : 400000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 322224-10414 |  | 1 | Individual selection
| dpcbcv failsafe electro |  |  | TA-Compact-DP 25 |  | 25 (1") | Thread male | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00011 m3/s |  |  |  |  | 15576 Pa |  | pos. 1.25 | 20576 Pa |  | 52164-225 |  | 1 | TA-Slider 160 Fail-safe R24 (1m HF) | Close-off Dp : 400000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | Relay 24V | Fail-safe type : Electronic | Fail-safe position : Configurable | Max. Temp. : 120°C | [8 empty] | 322224-10714 |  | 1 | Individual selection
| trv failsafe electro |  |  | Standard 10(3/8") |  | 10 (3/8") | Rad. union/Thread | Angle |  | PN10; -10/120 °C | [7 empty] | 4.167e-5 m3/s |  | 556 Pa | [5 empty] | Avail. Dp unknown |  | 2201-01.000 |  | 1 | TA-Slider 160 Fail-safe I/O (2m HF) | Max force : 160 N | Actuating time : 10 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | No relay | Fail-safe type : Electronic | Fail-safe position : Configurable | Max. Temp. : 120°C | [8 empty] | 322224-10615 |  | 1 | Individual selection
| trv failsafe electro | Return valve |  | TRIM A 15 |  | 15 (1/2") | Rad. union/Thread | Angle |  | PN16; -10/120 °C | [7 empty] | 4.167e-5 m3/s |  | 618 Pa |  |  |  |  | Setting = 5.25* |  |  | 50009-115 |  | 1
| trv failsafe no |  |  | Standard 10(3/8") |  | 10 (3/8") | Rad. union/Thread | Angle |  | PN10; -10/120 °C | [7 empty] | 4.167e-5 m3/s |  | 556 Pa | [5 empty] | Avail. Dp unknown |  | 2201-01.000 |  | 1 | TA-Slider 160 (5m HF) | Max force : 160 N | Actuating time : 10 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 322224-10116 |  | 1 | Individual selection
| trv failsafe no | Return valve |  | TRIM A 15 |  | 15 (1/2") | Rad. union/Thread | Angle |  | PN16; -10/120 °C | [7 empty] | 4.167e-5 m3/s |  | 618 Pa |  |  |  |  | Setting = 5.25* |  |  | 50009-115 |  | 1
| *A |  |  | STAF* 125 |  | 125 (5") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.012 m3/s |  | 3000 Pa |  |  |  |  | 6.7 turns |  |  | 52186-091 |  | 1 | [22 empty] | Hydraulic Network
| *A.1 |  |  | CV 216 RGA DN40 | Bronze | Kvs = 20 | Thread | Standard |  | PN16; -15/150 °C | [7 empty] | 0.0016 m3/s |  | 7840 Pa |  |  |  |  | - |  |  | 60233-140 |  | 1 | TA-Slider 750 Fail-safe Plus (HV) | Close-off Dp : 390909 Pa | Actuating time : 42; 56; 84; 112; 168; 224* s | IP auto(man.) : 54 | 115 VAC; 230 VAC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V; 0(4)-20 mA | Relay 220V | Fail-safe type : Electronic | Fail-safe position : Configurable | Max. Temp. : 120°C | [8 empty] | 322226-40319 |  | 1 | Hydraulic Network
| *A.1 |  |  | STAD* 50 |  | 50 (2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0016 m3/s |  | 5389 Pa |  |  |  |  | 3.24 turns |  |  | 52851-050 |  | 1 | [22 empty] | Hydraulic Network
| *A.2 |  |  | CV 206 GG DN65 | Cast iron | Kvs = 50 | Flange | Standard |  | PN6; -10/150 °C | [7 empty] | 0.0042 m3/s |  | 9000 Pa |  |  |  |  | - |  |  | 60215-165 |  | 1 | TA-MC 65Y | Close-off Dp : 100000 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61065-003 |  | 1 | Hydraulic Network
| *A.2 |  |  | STAF* 80 |  | 80 (3") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.0042 m3/s |  | 3000 Pa |  |  |  |  | 6.25 turns |  |  | 52186-080 |  | 1 | [22 empty] | Hydraulic Network
| *A.3 |  |  | CV 206 GG DN65 | Cast iron | Kvs = 50 | Flange | Standard |  | PN6; -10/150 °C | [7 empty] | 0.005 m3/s |  | 12960 Pa |  |  |  |  | - |  |  | 60215-165 |  | 1 | TA-MC 65Y | Close-off Dp : 100000 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61065-003 |  | 1 | Hydraulic Network
| *A.3 |  |  | STAF* 65 |  | 65 (2 1/2") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.005 m3/s |  | 13740 Pa |  |  |  |  | 5.55 turns |  |  | 52186-065 |  | 1 | [22 empty] | Hydraulic Network
| *A.3 | secondary |  | STAF* 80 |  | 80 (3") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.005 m3/s |  | 3000 Pa |  |  |  |  | 7 turns |  |  | 52186-080 |  | 1 | [22 empty] | Hydraulic Network
| *A.4 |  |  | TBV-CM 3/4"(20NF) | Ametal(tm) |  | Thread NPT | US specific |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  | 18184 Pa |  |  |  |  | pos. 9 |  |  | 52144-720 |  | 1 | EMO TM 24/NC (5m) | Close-off Dp : 380000 Pa | Actuating time : 120 s | IP auto(man.) : 54 | 24 VAC | 0(2)-10 V | - | No relay | Fail-safe type : No | Default return position : Extending | Max. Temp. : 120°C | [8 empty] | 1868-02.500 |  | 1 | Hydraulic Network
| *A.5 |  |  | TBV-CM 20NF | Ametal(tm) |  | Thread | Standard |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  | 18088 Pa |  |  |  |  | pos. 9 |  |  | 52144-120 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 322224-10111 |  | 1 | Hydraulic Network
| *A.6 |  |  | TBV-CM 3/4"(20NF) | Ametal(tm) |  | Thread NPT | US specific |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  | 17977 Pa |  |  |  |  | pos. 9 |  |  | 52144-720 |  | 1 | EMO TM 24/NC (0.8m) | Close-off Dp : 380000 Pa | Actuating time : 120 s | IP auto(man.) : 54 | 24 VAC | 0(2)-10 V | - | No relay | Fail-safe type : No | Default return position : Extending | Max. Temp. : 120°C | [8 empty] | 1868-00.500 |  | 1 | Hydraulic Network
| *A.7 |  |  | TBV-CM 3/4"(20NF) | Ametal(tm) |  | Thread NPT | US specific |  | PN16; -20/120 °C | [7 empty] | 0.00022 m3/s |  | 18249 Pa |  |  |  |  | pos. 9 |  |  | 52144-720 |  | 1 | TA-Slider 160 Fail-safe I/O (2m HF) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | No relay | Fail-safe type : Electronic | Fail-safe position : Configurable | Max. Temp. : 120°C | [8 empty] | 322224-10615 |  | 1 | Hydraulic Network

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-*** (deleted) |  |  | TA-MC 100FSE/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 2
*****-*** (deleted) |  |  | TA-MC 100FSR/230; Actuating force = 1000 N; Power Supply = 230 VAC; Relay type = No relay | 1
*****-****** (deleted) |  |  | TA-Fusion-P 32; Standard; Thread male; PN 16 | 1
*****-****** (deleted) |  |  | TA-Fusion-P 32; Standard; Thread; PN 16 | 4
1868-00.500 |  |  | EMO TM 24/NC (0.8m); Actuating force = 125 N; Power Supply = 24 VAC; Relay type = No relay | 1
1868-02.500 |  |  | EMO TM 24/NC (5m); Actuating force = 125 N; Power Supply = 24 VAC; Relay type = No relay | 1
2201-01.000 |  |  | Standard 10(3/8"); Angle; Thread; PN 10 | 2
322224-10111 |  |  | TA-Slider 160 (1m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 2
322224-10116 |  |  | TA-Slider 160 (5m HF); Actuating force = 160 N; 24 VAC; 24 VDC | 1
322224-10212 |  |  | TA-Slider 160 Plus (2m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = Relay 220V | 1
322224-10414 |  |  | TA-Slider 160 I/O (1m HF); Actuating force = 160 N; 24 VAC; 24 VDC | 1
322224-10513 |  |  | TA-Slider 160 CO (5m); Actuating force = 160 N; Power Supply = 24 VAC; Relay type = Relay change-over | 1
322224-10614 |  |  | TA-Slider 160 Fail-safe I/O (1m HF); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
322224-10615 |  |  | TA-Slider 160 Fail-safe I/O (2m HF); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 2
322224-10714 |  |  | TA-Slider 160 Fail-safe R24 (1m HF); Actuating force = 160 N; 24 VAC; 24 VDC | 2
322224-10715 |  |  | TA-Slider 160 Fail-safe R24 (2m HF); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = Relay 24V | 1
322226-10110 |  |  | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
322226-40219 |  |  | TA-Slider 750 Plus (HV); Actuating force = 750 N; Power Supply = 115 VAC; 230 VAC; Relay type = Relay 220V | 1
322226-40319 |  |  | TA-Slider 750 Fail-safe Plus (HV); Actuating force = 750 N; Power Supply = 115 VAC; 230 VAC; Relay type = Relay 220V | 3
322226-42219 |  |  | TA-Slider 750 Plus Modbus/RTU (HV); Actuating force = 750 N; Power Supply = 115 VAC; 230 VAC; Relay type = Relay 220V | 1
50009-115 |  |  | TRIM A 15; Angle; Thread; PN 16 | 2
52144-115 |  |  | TBV-CM 15NF; Standard; Thread; PN 16; Kvs = 1 | 1
52144-120 |  |  | TBV-CM 20NF; Standard; Thread; PN 16; Kvs = 2 | 4
52144-720 |  |  | TBV-CM 3/4"(20NF); Kvs = 2; US specific; Thread NPT | 3
52164-220 |  |  | TA-Compact-DP 20; [5000-17025] Pa; Standard; Thread male | 1
52164-225 |  |  | TA-Compact-DP 25; [5000-17173] Pa; Standard; Thread male | 1
52186-065 |  |  | STAF* 65; Standard; Flange; PN 16 | 1
52186-080 |  |  | STAF* 80; Standard; Flange; PN 16 | 2
52186-091 |  |  | STAF* 125; Standard; Flange; PN 16 | 1
52851-050 |  |  | STAD* 50; Without drain; Thread; PN 25 | 1
60215-165 |  |  | CV 206 GG DN65; Standard; Flange; PN 6; Kvs = 50 | 3
60233-140 |  |  | CV 216 RGA DN40; Kvs = 20; Standard; Thread | 1
60235-265 |  |  | CV 216 GG DN65; Standard; Flange; PN 16; Kvs = 63 | 2
61065-003 |  |  | TA-MC 65Y; Actuating force = 600 N; Power Supply = 24 VAC; Relay type = No relay | 2