## Valves export (1)
Technical informations | #1 |  | #2 | Primary product | [26 empty] | Secondary product | [21 empty] | Selection mode
|  |  |  | Product | [13 empty] | Technical informations | [9 empty] | Article N° | Local Art. Nr. | Qty | Product | [14 empty] | Technical informations |  |  |  | Article N° | Local Art. Nr. | Qty
|  |  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Location | Kvs | Qnom | Cable length to remote temp. sensor | Power Supply | Input | Output signal | Flow | Power/DT | Dp | Control mode | Dpl | Dp min. | Dp max. | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [9 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
| *A.1 |  |  | TA-Smart 125 | Ductile iron | 125 (5") | Flange | Standard |  | PN25; -10/110 °C | Return | 190 | 0.031 m3/s | 5 m | Power Supply : 24 VAC; 24 VDC | Input : 0(2)-10 V; 0(4)-20 mA; Modbus RTU; BACnet MSTP; Modbus TCP; BACnet IP | Output signal : 0(2)-10 V; Modbus RTU; BACnet MSTP; Modbus TCP; BACnet IP | 0.03 m3/s |  |  | Flow |  | 32294 Pa |  |  |  |  | 322231-01391 |  | 1 | [22 empty] | Hydraulic Network
| *A.1 | secondary |  | STAF* 150 |  | 150 (6") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.03 m3/s |  | 7286 Pa |  |  |  |  | 8* turns |  |  | 52186-092 |  | 1 | [22 empty] | Hydraulic Network
| *A.1.1 |  |  | TA-Smart 125 | Ductile iron | 125 (5") | Flange | Standard |  | PN25; -10/110 °C | Supply | 190 | 0.031 m3/s | 5 m | Power Supply : 24 VAC; 24 VDC | Input : 0(2)-10 V; 0(4)-20 mA; Modbus RTU; BACnet MSTP; Modbus TCP; BACnet IP | Output signal : 0(2)-10 V; Modbus RTU; BACnet MSTP; Modbus TCP; BACnet IP | 0.03 m3/s | 751488 W / 6 °C |  | Power |  | 32310 Pa |  |  |  |  | 322231-01391 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1 |  | VPA/C2/B2/001 | STAP 50 |  | 50 (2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0025 m3/s |  |  |  | Dpl = 51014 Pa | 13773 Pa |  | 30 turns | 72660 Pa |  | 52265-050 |  | 1 | STAD* 50 | [10 empty] | 50 (2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.0025 m3/s |  | 7873 Pa | 4* turns | 52851-650 |  | 1 | Hydraulic Network
| *A.2.1.1 |  | domestic water HEX | STAD* 50 |  | 50 (2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0013 m3/s |  | 3000 Pa |  |  |  |  | 3.41 turns |  |  | 52851-050 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.2.1 |  | C2/B2/ME/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 22514 Pa |  |  |  |  | 2.62 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.2.2 |  | C2/B2/WT/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 22206 Pa |  |  |  |  | 2.63 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.2.3 |  | C2/B2/WT/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 22155 Pa |  |  |  |  | 2.63 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.3 |  | C2/B2/CO/15B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 23508 Pa |  |  |  |  | 3.26 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.4.1 |  | C2/B2/CO/15A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 18271 Pa |  |  |  |  | 2.74 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.4.2 |  | C2/B2/CO/16 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.6e-5 m3/s |  | 14410 Pa |  |  |  |  | 2.76 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.4.3 |  | C2/B2/LV/01B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00019 m3/s |  | 13417 Pa |  |  |  |  | 3.36 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.4.4 |  | C2/B2/LV/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00019 m3/s |  | 12361 Pa |  |  |  |  | 3.43 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.5 |  | C2/B2/LV/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9.7e-5 m3/s |  | 17002 Pa |  |  |  |  | 3.06 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.6 |  | C2/B2/UPS/1 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.5e-5 m3/s |  | 16082 Pa |  |  |  |  | 2.15 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.7 |  | C2/B2/FSE/1 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 1e-5 m3/s |  | 16168 Pa |  |  |  |  | 0.97 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.8 |  | C2/B2/BTER/1B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9.1e-5 m3/s |  | 15243 Pa |  |  |  |  | 3.05 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.1.9 |  | C2/B2/BTER/1A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9.1e-5 m3/s |  | 15039 Pa |  |  |  |  | 3.06 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2 |  | VPA/C2/B2/001 | STAP 50 |  | 50 (2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0027 m3/s |  |  |  | Dpl = 54276 Pa | 16204 Pa |  | 32.5 turns | 79739 Pa |  | 52265-050 |  | 1 | STAD* 50 | [10 empty] | 50 (2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.0027 m3/s |  | 9260 Pa | 4* turns | 52851-650 |  | 1 | Hydraulic Network
| *A.2.2.1.1 |  | C2/B2/TR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.5e-5 m3/s |  | 24925 Pa |  |  |  |  | 2.36 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.1.2 |  | C2/B2/CO/02B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.6e-5 m3/s |  | 24362 Pa |  |  |  |  | 2.77 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%P |  | C2/B2/LR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.6e-5 m3/s |  | 21680 Pa |  |  |  |  | 2.82 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%O |  | C2/B2/LR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.4e-5 m3/s |  | 19990 Pa |  |  |  |  | 2.83 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%L |  | C2/B2/PR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.1e-5 m3/s |  | 18844 Pa |  |  |  |  | 2.58 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%N |  | C2/B2/PR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 17110 Pa |  |  |  |  | 2.98 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%M |  | C2/B2/CO/17 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.5e-5 m3/s |  | 15614 Pa |  |  |  |  | 2.57 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.1.4 |  | C2/B2/RC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 19820 Pa |  |  |  |  | 3.24 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.1.5 |  | C2/B2/FAD/1 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.2e-5 m3/s |  | 17637 Pa |  |  |  |  | 2.03 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.1.6 |  | C2/B2/SER/1 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 17730 Pa |  |  |  |  | 3.07 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.2 |  | C2/B2/SR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9.5e-5 m3/s |  | 24794 Pa |  |  |  |  | 2.85 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.3 |  | C2/B2/CO/15C | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 21481 Pa |  |  |  |  | 3.31 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.4 |  | C2/B2/SR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.1e-5 m3/s |  | 18534 Pa |  |  |  |  | 2.72 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.1 |  | C2/B2/BR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.4e-5 m3/s |  | 12830 Pa |  |  |  |  | 1.93 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.2 |  | C2/B2/SR/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 8223 Pa |  |  |  |  | 3.12 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.3 |  | C2/B2/CO/14B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 6412 Pa |  |  |  |  | 3.4 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.4 |  | C2/B2/HV/01B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00012 m3/s |  | 6109 Pa |  |  |  |  | 3.24 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.5 |  | C2/B2/CO/14A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4836 Pa |  |  |  |  | 3.66 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.5.6 |  | C2/B2/HW/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00012 m3/s |  | 4209 Pa |  |  |  |  | 3.53 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.6 |  | C2/B2/CO/14C | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 14589 Pa |  |  |  |  | 2.85 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.7.1 |  | C2/B2/SR/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.5e-5 m3/s |  | 12915 Pa |  |  |  |  | 2.48 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.7.2 |  | C2/B2/CO/13 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 12103 Pa |  |  |  |  | 2.9 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.8 |  | C2/B2/CO/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.9e-5 m3/s |  | 11580 Pa |  |  |  |  | 2.4 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.9 |  | C2/B2/CW/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 10832 Pa |  |  |  |  | 2.78 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.10 |  | C2/B2/CW/MP01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 6894 Pa |  |  |  |  | 3.31 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%K |  | C2/B2/CT/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 5740 Pa |  |  |  |  | 3.4 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%J |  | C2/B2/CT/01E | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 3000 Pa |  |  |  |  | 2.5 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.12 |  | C2/B2/CO/12 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 4334 Pa |  |  |  |  | 3.42 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.2.2.13 |  | C2/B2/CT/01B | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 3317 Pa |  |  |  |  | 2.42 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.3 |  | VPA/C2/B1/002 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0013 m3/s |  |  |  | Dpl = 54658 Pa | 14196 Pa |  | 32.5 turns | 75183 Pa |  | 52265-040 |  | 1 | STAF-SG 40 | [10 empty] | 40 (1 1/2") | Flange | Standard | PN16/25; -10/120 °C | 0.0013 m3/s |  | 6329 Pa | 4* turns | 52182-040 |  | 1 | Hydraulic Network
| *A.3.1.1 |  | C2/B1/LB/01A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 28712 Pa |  |  |  |  | 2.87 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.2 |  | C2/B1/LB/01B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 27089 Pa |  |  |  |  | 2.89 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.3 |  | C2/B1/STO/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.5e-5 m3/s |  | 26549 Pa |  |  |  |  | 2.72 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.4 |  | C2/B1/CO/09C | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00015 m3/s |  | 23310 Pa |  |  |  |  | 2.73 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.5 |  | C2/B1/CO/09B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00015 m3/s |  | 20062 Pa |  |  |  |  | 2.81 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.6 |  | C2/B1/CO/09A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00015 m3/s |  | 19019 Pa |  |  |  |  | 2.84 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.7 |  | C2/B1/CO/11B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.6e-5 m3/s |  | 19268 Pa |  |  |  |  | 2.5 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.8 |  | C2/B1/SR/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.6e-5 m3/s |  | 16989 Pa |  |  |  |  | 2.55 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.1.9 |  | C2/B1/CO/11A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.6e-5 m3/s |  | 16961 Pa |  |  |  |  | 2.55 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.2 |  | C2/B1/CO/06A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 28803 Pa |  |  |  |  | 3.1 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.3 |  | C2/B1/CO/06B | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00013 m3/s |  | 3000 Pa |  |  |  |  | 2.51 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.4 |  | C2/B1/LR/01A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.6e-5 m3/s |  | 24792 Pa |  |  |  |  | 2.65 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.3.5 |  | C2/B1/LR/01B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.6e-5 m3/s |  | 31198 Pa |  |  |  |  | 2.55 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.4 |  | C2/02/B1/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 86547 Pa |  |  |  |  | 1.56 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5 |  | VPA/C2/B1/002 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.001 m3/s |  |  |  | Dpl = 37238 Pa | 8551 Pa |  | 19.5 turns | 49569 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.001 m3/s |  | 3780 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.5.1.1 |  | C2/B1/ME/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 12568 Pa |  |  |  |  | 2.88 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%H |  | C2/B1/SR/03A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.2e-5 m3/s |  | 11693 Pa |  |  |  |  | 2.8 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%F |  | C2/B1/SR/02A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.3e-5 m3/s |  | 11051 Pa |  |  |  |  | 2.99 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%I |  | C2/B1/SR/03B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.2e-5 m3/s |  | 9743 Pa |  |  |  |  | 2.89 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%G |  | C2/B1/SR/02B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.3e-5 m3/s |  | 8864 Pa |  |  |  |  | 3.1 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.1.4 |  | C2/B1/ME/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 7259 Pa |  |  |  |  | 3.16 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.2 |  | C2/B1/CO/10 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4e-5 m3/s |  | 14351 Pa |  |  |  |  | 2.33 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.3.1 |  | C2/B1/TR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.2e-5 m3/s |  | 12751 Pa |  |  |  |  | 2.76 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.3.2 |  | C2/B1/CO/13 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 10627 Pa |  |  |  |  | 2.97 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.3.3 |  | C2/B1/CO4/12B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.2e-5 m3/s |  | 8280 Pa |  |  |  |  | 3.25 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.3.4 |  | C2/B1/COR/12A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.2e-5 m3/s |  | 7955 Pa |  |  |  |  | 3.28 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.4 |  | C2/B1/STO/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6e-5 m3/s |  | 7683 Pa |  |  |  |  | 2.97 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.5.1 |  | C2/B1/WC/01B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.6e-5 m3/s |  | 6026 Pa |  |  |  |  | 3.65 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.5.2 |  | C2/B1/WC/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.6e-5 m3/s |  | 6157 Pa |  |  |  |  | 2.81 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.5.6 |  | C2/B1/SR/05 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.2e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.76 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.6.1 |  | AHU/C2/B1/01 | KTM 512 DN25/32 LF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.00073 m3/s |  |  |  |  | 20624 Pa |  | 4.45 turns |  |  | 52796-225&2*52759-025 |  | 1 | TA-R25-F24 | Max. inlet pressure : 573885 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.6.2 |  | AHU/C2/B1/02 | KTM 512 DN40/50 NF | Ductile iron |  | Thread male | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.0026 m3/s |  |  |  |  | 39349 Pa |  | 9.6 turns |  |  | 52796-040&2*52759-140 |  | 1 | TA-R25-F24 | Max. inlet pressure : 100000 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.7.1.1 |  | AHU/C2/01/01W | KTM 512 DN100 NF | Ductile iron |  | Flange | PT 90 |  | PN16; -10/120 °C | [7 empty] | 0.011 m3/s |  |  |  |  | 36729 Pa |  | 9.36 turns |  |  | 52791-590 |  | 1 | TA-NV24 | Max. inlet pressure : 2.350425e+6 Pa | Actuating time : 150 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 3-point; 0-10 V | 2-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 50358-020 |  | 1 | Hydraulic Network
| *A.7.1.2 |  | AHU/C2/B2/02 | KTM 512 DN40/50 NF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.0026 m3/s |  |  |  |  | 39045 Pa |  | 9.35 turns |  |  | 52796-040&2*52759-040 |  | 1 | TA-R25-F24 | Max. inlet pressure : 100000 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.7.1.3 |  | AHU/C2/B2/01 | KTM 512 DN40/50 NF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.0023 m3/s |  |  |  |  | 35219 Pa |  | 7 turns |  |  | 52796-040&2*52759-040 |  | 1 | TA-R25-F24 | Max. inlet pressure : 100000 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.7.2 |  | AHU/C2/00/02W | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0036 m3/s |  |  |  |  | 20479 Pa |  | 8.24 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.7.3 |  | AHU/C2/00/04W | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0027 m3/s |  |  |  |  | 16641 Pa |  | 6.78 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.7.4 |  | AHU/C2/00/03W | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0035 m3/s |  |  |  |  | 19720 Pa |  | 7.92 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.8.1 |  | VPA/C2/00/003 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.001 m3/s |  |  |  | Dpl = 34765 Pa | 8209 Pa |  | 17 turns | 46604 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.001 m3/s |  | 3629 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.8.1.1 |  | C2/01/CO/09B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 12306 Pa |  |  |  |  | 3.15 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.2.1 |  | C2/01/CO/20 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.3e-5 m3/s |  | 5487 Pa |  |  |  |  | 3.36 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.2.2 |  | C2/01/LR/06A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 7235 Pa |  |  |  |  | 3.03 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.2.3 |  | C2/01/LR/06B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 6764 Pa |  |  |  |  | 3.08 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.3 |  | C2/01/SR/09 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 8599 Pa |  |  |  |  | 2.93 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.4.1 |  | C2/01/CO/12B | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00016 m3/s |  | 5137 Pa |  |  |  |  | 2.43 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.4.2 |  | C2/01/CO/12A | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00016 m3/s |  | 3273 Pa |  |  |  |  | 2.77 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.5 |  | C2/01/TR/04 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4882 Pa |  |  |  |  | 2.75 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.6 |  | C2/01/CO/14A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.1e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.68 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.1.7 |  | C2/01/CO/14B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.1e-5 m3/s |  | 3458 Pa |  |  |  |  | 2.76 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2 |  | VPA/C2/00/002 | STAP 80 |  | 80 (3") | Flange | Standard | [20000-80000] Pa | PN16; -10/120 °C | [7 empty] | 0.0055 m3/s |  |  |  | Dpl = 33491 Pa | 12766 Pa |  | 25 turns | 49256 Pa |  | 52265-080 |  | 1 | STAF* 80 | [10 empty] | 80 (3") | Flange | Standard | PN16; -10/120 °C | 0.0055 m3/s |  | 3000 Pa | 7.45 turns | 52186-080 |  | 1 | Hydraulic Network
| *A.8.2.1.1 |  | C2/00/CN/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5747 Pa |  |  |  |  | 3.53 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BK |  | C2/00/RL/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5766 Pa |  |  |  |  | 3.53 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BL |  | C2/00/RL/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 6029 Pa |  |  |  |  | 3.49 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.3 |  | C2/00/ER/07 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5637 Pa |  |  |  |  | 3.55 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BB |  | C2/00/RL/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5637 Pa |  |  |  |  | 3.55 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BC |  | C2/00/RL/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5901 Pa |  |  |  |  | 3.51 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.5 |  | C2/00/ER/08 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5335 Pa |  |  |  |  | 3.61 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.6 |  | C2/00/OR/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5294 Pa |  |  |  |  | 3.61 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.7 |  | C2/00/IN/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5236 Pa |  |  |  |  | 3.62 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.8 |  | C2/00/ER/09 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5169 Pa |  |  |  |  | 3.64 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.1.9 |  | C2/00/ER/10 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5136 Pa |  |  |  |  | 3.65 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BM |  | C2/00/IN/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4914 Pa |  |  |  |  | 3.69 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BN |  | C2/00/NW/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4833 Pa |  |  |  |  | 3.71 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BJ |  | C2/00/IN/03 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4772 Pa |  |  |  |  | 3.73 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BH |  | C2/00/ER/12 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 9101 Pa |  |  |  |  | 3.17 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BI |  | C2/00/ER/11 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3180 Pa |  |  |  |  | 2.57 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| Named%BD |  | C2/00/OC/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3000 Pa |  |  |  |  | 2.61 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| Named%BE |  | C2/00/IN/04 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3263 Pa |  |  |  |  | 2.55 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| Named%BF |  | C2/00/ER/13 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5128 Pa |  |  |  |  | 3.65 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%BG |  | C2/00/TR/04 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 5391 Pa |  |  |  |  | 3.59 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.2 |  | C2/00/NT/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4839 Pa |  |  |  |  | 3.71 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.3 |  | C2/00/NT/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4757 Pa |  |  |  |  | 3.73 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.4 |  | C2/00/OM/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4696 Pa |  |  |  |  | 2.26 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.5 |  | C2/00/IS/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4555 Pa |  |  |  |  | 2.29 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.6 |  | C2/00/WT/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4520 Pa |  |  |  |  | 2.29 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.7 |  | C2/00/PT/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 8651 Pa |  |  |  |  | 3.21 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.2.8 |  | C2/00/MD/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3028 Pa |  |  |  |  | 2.6 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.3 |  | C2/00/ER/06 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4550 Pa |  |  |  |  | 2.29 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.4 |  | C2/00/ER/05 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4509 Pa |  |  |  |  | 2.29 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.5 |  | C2/00/ER/04 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4450 Pa |  |  |  |  | 2.3 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.6 |  | C2/00/HIM/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4383 Pa |  |  |  |  | 2.32 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.7 |  | C2/00/CO/06 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4350 Pa |  |  |  |  | 2.32 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.8 |  | C2/00/PO/12 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4128 Pa |  |  |  |  | 2.36 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.9 |  | C2/00/ER/03 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 4047 Pa |  |  |  |  | 2.38 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.10 |  | C2/00/ER/02 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3986 Pa |  |  |  |  | 2.39 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.11 |  | C2/00/PO/11 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3844 Pa |  |  |  |  | 2.42 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.12 |  | C2/00/ER/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3809 Pa |  |  |  |  | 2.43 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.13 |  | C2/00/CO/07 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3628 Pa |  |  |  |  | 2.47 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.2.14 |  | C2/00/ER/17 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 3892 Pa |  |  |  |  | 2.41 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3 |  | VPA/C2/00/001 | STAP 65 |  | 65 (2 1/2") | Flange | Standard | [40000-160000] Pa | PN16; -10/120 °C | [7 empty] | 0.0033 m3/s |  |  |  | Dpl = 84922 Pa | 10661 Pa |  | 42.5 turns | 98584 Pa |  | 52265-165 |  | 1 | STAF* 65 | [10 empty] | 65 (2 1/2") | Flange | Standard | PN16; -10/120 °C | 0.0033 m3/s |  | 3000 Pa | 6.6 turns | 52186-065 |  | 1 | Hydraulic Network
| Named%BA |  | C2/00/PH/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 48977 Pa |  |  |  |  | 2.89 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%X |  | C2/00/REC/03B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 48097 Pa |  |  |  |  | 2.9 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%Z |  | C2/00/REC/03A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 46343 Pa |  |  |  |  | 2.92 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%Y |  | C2/00/LOU/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 40721 Pa |  |  |  |  | 2.99 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%W |  | C2/00/HE/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 49400 Pa |  |  |  |  | 2.89 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%V |  | C2/00/WO/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 47645 Pa |  |  |  |  | 2.91 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%U |  | C2/00/WH/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 42023 Pa |  |  |  |  | 2.97 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.1.3 |  | C2/00/CO/05 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 44028 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%T |  | C2/00/MR/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 48317 Pa |  |  |  |  | 2.9 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%S |  | C2/00/MR/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 42695 Pa |  |  |  |  | 2.96 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%R |  | C2/00/CBO/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 48150 Pa |  |  |  |  | 2.9 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%Q |  | C2/00/WR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 42528 Pa |  |  |  |  | 2.96 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.1.6 |  | C2/00/PR/02D | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 43566 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.1.7 |  | C2/00/PR/02B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 43531 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.1.8 |  | C2/00/PR/02A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 43351 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.1.9 |  | C2/00/PR/02C | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 43614 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.2 |  | C2/00/CW/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 49136 Pa |  |  |  |  | 1.21 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.3 |  | C2/00/CNO/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 47671 Pa |  |  |  |  | 2.61 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.4 |  | C2/00/CC/09 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 43046 Pa |  |  |  |  | 1.33 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.5 |  | C2/00/CC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 41153 Pa |  |  |  |  | 2.68 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.6 |  | C2/00/CC/08 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 38037 Pa |  |  |  |  | 1.41 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.7 |  | C2/00/CC/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 36328 Pa |  |  |  |  | 2.73 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.8 |  | C2/00/CC/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 30718 Pa |  |  |  |  | 1.5 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.9 |  | C2/00/CC/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 28686 Pa |  |  |  |  | 2.84 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.10 |  | C2/00/CC/06 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 25291 Pa |  |  |  |  | 1.58 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.11 |  | C2/00/CC/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 23537 Pa |  |  |  |  | 2.93 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.12 |  | C2/00/CC/05 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.7e-5 m3/s |  | 20973 Pa |  |  |  |  | 2.08 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.13 |  | C2/00/CG/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 22510 Pa |  |  |  |  | 2.64 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.14 |  | C2/00/PS/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.5e-5 m3/s |  | 19711 Pa |  |  |  |  | 2.47 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.15 |  | C2/00/LL/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 16088 Pa |  |  |  |  | 3.19 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.16 |  | C2/00/LR/01B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 5350 Pa |  |  |  |  | 2.7 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.8.3.17 |  | C2/00/LR/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.03 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.9.1 |  | AHU/C2/01/01W | KTM 512 DN65 NF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0048 m3/s |  |  |  |  | 32456 Pa |  | 7.8 turns |  |  | 52791-865 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.051275e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.9.2 |  | AHU/C2/01/02W | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0041 m3/s |  |  |  |  | 22720 Pa |  | 9.3 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.9.3 |  | AHU/C2/01/04W | KTM 512 DN100 LF | Ductile iron |  | Flange | PT 90 |  | PN16; -10/120 °C | [7 empty] | 0.0067 m3/s |  |  |  |  | 22073 Pa |  | 9.32 turns |  |  | 52791-490 |  | 1 | TA-Slider 750 (24V) | Max. inlet pressure : 2.5e+6 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 322226-10110 |  | 1 | Hydraulic Network
| *A.9.4 |  | AHU/C2/01/03W | KTM 512 DN40/50 LF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.00091 m3/s |  |  |  |  | 14226 Pa |  | 4.85 turns |  |  | 52796-240&2*52759-040 |  | 1 | TA-R25-F24 | Max. inlet pressure : 283440 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.9.5 |  |  | STAP 100 |  | 100 (4") | Flange | Standard | [40000-160000] Pa | PN16; -10/120 °C | [7 empty] | 0.016 m3/s |  |  |  | Dpl = 78928 Pa | 27406 Pa |  | 52 turns | 116028 Pa |  | 52265-190 |  | 1 | STAF* 100 | [10 empty] | 100 (4") | Flange | Standard | PN16; -10/120 °C | 0.016 m3/s |  | 9694 Pa | 8* turns | 52186-090 |  | 1 | Hydraulic Network
| *A.9.5.1 |  | provision for LVL.2 kitchen | STAF* 125 |  | 125 (5") | Flange | Standard |  | PN16; -10/120 °C | [7 empty] | 0.014 m3/s |  | 3000 Pa |  |  |  |  | 7.9* turns |  |  | 52186-091 |  | 1 | [22 empty] | Hydraulic Network
| *A.9.5.2 |  | provision for LVL.2 dining | STAD* 50 |  | 50 (2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.002 m3/s |  | 6930 Pa |  |  |  |  | 3.53 turns |  |  | 52851-050 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.1 |  | C2/01/RC/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 75581 Pa |  |  |  |  | 2.31 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.2 |  | VPA/C2/01/002 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.001 m3/s |  |  |  | Dpl = 34765 Pa | 8209 Pa |  | 17.5 turns | 46604 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.001 m3/s |  | 3629 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.10.2.1 |  | C2/01/CO/09B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 12306 Pa |  |  |  |  | 3.15 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%C |  | C2/01/CO/20 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.3e-5 m3/s |  | 5487 Pa |  |  |  |  | 3.36 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| Named%E |  | C2/01/LR/06A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 7235 Pa |  |  |  |  | 3.03 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%D |  | C2/01/LR/06B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 6764 Pa |  |  |  |  | 3.08 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.2.3 |  | C2/01/SR/09 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 8599 Pa |  |  |  |  | 2.93 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| Named%B |  | C2/01/CO/12B | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00016 m3/s |  | 5137 Pa |  |  |  |  | 2.43 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| Named%A |  | C2/01/CO/12A | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00016 m3/s |  | 3273 Pa |  |  |  |  | 2.77 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.2.5 |  | C2/01/TR/04 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4882 Pa |  |  |  |  | 2.75 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.2.6 |  | C2/01/CO/14A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.1e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.68 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.2.7 |  | C2/01/CO/14B | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.1e-5 m3/s |  | 3458 Pa |  |  |  |  | 2.76 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3 |  | VPA/C2/01/001 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0013 m3/s |  |  |  | Dpl = 59892 Pa | 13734 Pa |  | 36 turns | 79686 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.0013 m3/s |  | 6061 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.10.3.1.1 |  | C2/01/ME/02A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 27683 Pa |  |  |  |  | 3.18 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.1.2 |  | C2/01/ME/02B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 28773 Pa |  |  |  |  | 3.16 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.1.3 |  | C2/01/ME/02C | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00014 m3/s |  | 23151 Pa |  |  |  |  | 3.28 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.2 |  | C2/01/SR/08 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 26635 Pa |  |  |  |  | 1.56 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.3 |  | C2/01/CO/23 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 24344 Pa |  |  |  |  | 2.92 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.4 |  | C2/01/SR/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.7e-5 m3/s |  | 21584 Pa |  |  |  |  | 2.07 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.5 |  | C2/01/TR/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 22990 Pa |  |  |  |  | 2.64 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.6 |  | C2/01/SR/06 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.5e-5 m3/s |  | 22137 Pa |  |  |  |  | 2.42 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.7 |  | C2/01/LR/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 18189 Pa |  |  |  |  | 3.13 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.8 |  | C2/01/RC/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 9926 Pa |  |  |  |  | 3.03 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.9 |  | C2/01/RC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 8690 Pa |  |  |  |  | 3.1 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.10.3.10 |  | for future extension | STAD* 25 |  | 25 (1") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00036 m3/s |  | 3000 Pa |  |  |  |  | 3.35 turns |  |  | 52851-025 |  | 1 | [22 empty] | Hydraulic Network
| *A.11 |  | VPA/C2/02/002 | DA 516 DN25/32 |  | 32 (1 1/4") | Thread | PT 90 | [10000-100000] Pa | PN25; -10/120 °C | [7 empty] | 0.0016 m3/s |  |  |  | Dpl = 54804 Pa | 22371 Pa |  | 7.5 turns | 93166 Pa |  | 52795-225&2*52759-032 |  | 1 | STAF-SG 32 | [10 empty] | 32 (1 1/4") | Flange | Standard | PN16/25; -10/120 °C | 0.0016 m3/s |  | 15991 Pa | 4* turns | 52182-032 |  | 1 | Hydraulic Network
| *A.11.1 |  | C2/02/GS/15 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 29054 Pa |  |  |  |  | 1.96 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.2 |  | C2/02/GS/14 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 27798 Pa |  |  |  |  | 1.98 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.3.1 |  | C2/02/CO/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.9e-5 m3/s |  | 27306 Pa |  |  |  |  | 2.64 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.3.2 |  | C2/02/OF/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.9e-5 m3/s |  | 27284 Pa |  |  |  |  | 1.78 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.3.3 |  | C2/02/OF/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.9e-5 m3/s |  | 26893 Pa |  |  |  |  | 1.79 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.4 |  | C2/02/CO/08A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5e-5 m3/s |  | 26142 Pa |  |  |  |  | 2.25 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.5.1 |  | C2/02/CO/08B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5e-5 m3/s |  | 25827 Pa |  |  |  |  | 2.26 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.5.2 |  | C2/02/CO/09A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.9e-5 m3/s |  | 24860 Pa |  |  |  |  | 2.57 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.6 |  | C2/02/GS/13 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 25571 Pa |  |  |  |  | 2.02 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.7.1 |  | C2/02/OC/05 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 21093 Pa |  |  |  |  | 2.67 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.7.2 |  | C2/02/MS/01B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 24098 Pa |  |  |  |  | 3.03 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.7.3 |  | C2/02/MS/01A | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 23945 Pa |  |  |  |  | 3.03 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.8 |  | C2/02/GS/12 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 23978 Pa |  |  |  |  | 2.04 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.9 |  | C2/02/GS/11 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 22545 Pa |  |  |  |  | 2.07 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.10 |  | C2/02/EC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.2e-5 m3/s |  | 21221 Pa |  |  |  |  | 1.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.11 |  | C2/02/GS/10 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 21364 Pa |  |  |  |  | 2.1 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.12.1 |  | C2/02/GS/09 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 20273 Pa |  |  |  |  | 2.12 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.12.2 |  | C2/02/ST/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 18310 Pa |  |  |  |  | 3.1 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.13 |  | C2/02/00/09B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 13733 Pa |  |  |  |  | 2.84 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.14 |  | KITCHEN FCU'S | STAD* 25 |  | 25 (1") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00036 m3/s |  | 3000 Pa |  |  |  |  | 3.35 turns |  |  | 52851-025 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.15 |  | C2/02/TR/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 7928 Pa |  |  |  |  | 3.14 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.11.16 |  | C2/02/TR/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7e-5 m3/s |  | 5642 Pa |  |  |  |  | 3.29 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.12 |  | C2/02/GS/16 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 67720 Pa |  |  |  |  | 1.65 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.13 |  | C2/02/TR/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 67024 Pa |  |  |  |  | 2.36 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.14 |  | VPA/C2/02/001 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0012 m3/s |  |  |  | Dpl = 36115 Pa | 10971 Pa |  | 19.5 turns | 51931 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.0012 m3/s |  | 4845 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.14.1 |  | C2/02/OF/01A | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00012 m3/s |  | 11363 Pa |  |  |  |  | 2.84 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.2 |  | C2/02/OF/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00012 m3/s |  | 11365 Pa |  |  |  |  | 2.87 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.3 |  | C2/02/OFC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 7987 Pa |  |  |  |  | 3.14 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.4.1 |  | C2/02/OF/01B | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 6953 Pa |  |  |  |  | 3.21 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.4.2 |  | C2/02/CON/01 | STAD* 20 |  | 20 (3/4") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0002 m3/s |  | 7150 Pa |  |  |  |  | 2.53 turns |  |  | 52851-020 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.5 |  | C2/02/OFC/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 6742 Pa |  |  |  |  | 3.23 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.6 |  | C2/02/OFC/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 5756 Pa |  |  |  |  | 3.32 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.7 |  | C2/02/HC/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8e-5 m3/s |  | 6086 Pa |  |  |  |  | 2.74 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.8 |  | C2/02/HC/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8e-5 m3/s |  | 5567 Pa |  |  |  |  | 2.79 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.9 |  | C2/02/OF/01C | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00012 m3/s |  | 3722 Pa |  |  |  |  | 3.66 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.10 |  | C2/02/AD/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.03 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.14.11 |  | C2/02/AAD/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 3720 Pa |  |  |  |  | 3.18 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15 |  | VPA/C2/03/001 | STAP 32 |  | 32 (1 1/4") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0006 m3/s |  |  |  | Dpl = 36830 Pa | 6433 Pa |  | 19 turns | 46263 Pa |  | 52265-032 |  | 1 | STAD* 32 | [10 empty] | 32 (1 1/4") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.0006 m3/s |  | 3000 Pa | 3.63 turns | 52851-632 |  | 1 | Hydraulic Network
| *A.15.1 |  | C2/03/TR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00011 m3/s |  | 14875 Pa |  |  |  |  | 3.28 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.2 |  | C2/03/AD/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4917 Pa |  |  |  |  | 2.74 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.3 |  | C2/03/AD/02 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4716 Pa |  |  |  |  | 2.77 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.4 |  | C2/03/AD/03 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4046 Pa |  |  |  |  | 2.85 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.5 |  | C2/03/BM/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 4935 Pa |  |  |  |  | 3 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.6 |  | C2/03/RP/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.0001 m3/s |  | 3922 Pa |  |  |  |  | 3.29 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.15.7 |  | C2/03/OD/01 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8.1e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.19 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.16 |  | VPA/C2/03/002 | STAP 20 |  | 20 (3/4") | Thread | Standard | [10000-60000] Pa | PN16; -20/120 °C | [7 empty] | 0.00024 m3/s |  |  |  | Dpl = 35468 Pa | 7829 Pa |  | 27.5 turns | 46296 Pa |  | 52265-020 |  | 1 | STAD* 20 | [10 empty] | 20 (3/4") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.00024 m3/s |  | 3000 Pa | 3.79 turns | 52851-620 |  | 1 | Hydraulic Network
| *A.16.1 |  | C2/03/TE/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.5e-5 m3/s |  | 13253 Pa |  |  |  |  | 1.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.2 |  | C2/03/TE/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.2e-5 m3/s |  | 12679 Pa |  |  |  |  | 1.87 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.3 |  | C2/03/TE/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.1e-5 m3/s |  | 10351 Pa |  |  |  |  | 1.91 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.4 |  | C2/03/TE/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 2.5e-5 m3/s |  | 9629 Pa |  |  |  |  | 2.08 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.5 |  | C2/03/CO/05 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 8e-5 m3/s |  | 6160 Pa |  |  |  |  | 2.74 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.6 |  | C2/03/SS/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3e-5 m3/s |  | 5698 Pa |  |  |  |  | 2.49 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.16.7 |  | C2/03/TM/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 3.8e-5 m3/s |  | 3000 Pa |  |  |  |  | 2.99 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1 |  | VPA/C2/04/002 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.00095 m3/s |  |  |  | Dpl = 34924 Pa | 7075 Pa |  | 17.5 turns | 45129 Pa |  | 52265-040 |  | 1 | STAD* 40 | [10 empty] | 40 (1 1/2") | Thread | With drain 3/4" | PN25; -20/120 °C | 0.00095 m3/s |  | 3129 Pa | 4* turns | 52851-640 |  | 1 | Hydraulic Network
| *A.17.1.1 |  | C2/04/ST/02 | STAD* 25 |  | 25 (1") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 0.00049 m3/s |  | 6930 Pa |  |  |  |  | 3.05 turns |  |  | 52851-025 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.2 |  | C2/04/TR/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 6.8e-5 m3/s |  | 7111 Pa |  |  |  |  | 3.14 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.3 |  | C2/04/CW/16 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 7130 Pa |  |  |  |  | 2.78 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.4 |  | C2/04/CW/15 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4715 Pa |  |  |  |  | 2.77 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.5 |  | C2/04/CW/14 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 4015 Pa |  |  |  |  | 2.86 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.6 |  | C2/04/CW/13 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.2e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.03 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.1.7 |  | C2/04/CW/12 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 7.7e-5 m3/s |  | 4728 Pa |  |  |  |  | 2.84 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2 |  | VPA/C2/04/001 | STAP 40 |  | 40 (1 1/2") | Thread | Standard | [20000-80000] Pa | PN16; -20/120 °C | [7 empty] | 0.0015 m3/s |  |  |  | Dpl = 38249 Pa | 17860 Pa |  | 23 turns | 64067 Pa |  | 52265-040 |  | 1 | STAF-SG 40 | [10 empty] | 40 (1 1/2") | Flange | Standard | PN16/25; -10/120 °C | 0.0015 m3/s |  | 7958 Pa | 4* turns | 52182-040 |  | 1 | Hydraulic Network
| *A.17.2.1 |  | C2/04/CW/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 13806 Pa |  |  |  |  | 3.09 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.2 |  | C2/04/CW/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 13271 Pa |  |  |  |  | 3.11 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.3 |  | C2/04/CW/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 12798 Pa |  |  |  |  | 3.13 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.4 |  | C2/04/CW/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 12335 Pa |  |  |  |  | 3.14 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.5 |  | C2/04/CW/05 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 11899 Pa |  |  |  |  | 3.16 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.6 |  | C2/04/CW/06 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 11574 Pa |  |  |  |  | 3.18 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.7 |  | C2/04/CW/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 10272 Pa |  |  |  |  | 3.24 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.8 |  | C2/04/CW/08 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 9501 Pa |  |  |  |  | 3.28 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.9 |  | C2/04/CW/09 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 8833 Pa |  |  |  |  | 3.33 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.10 |  | C2/04/CW/10 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 8337 Pa |  |  |  |  | 2.7 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.11 |  | C2/04/CW/11 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 7300 Pa |  |  |  |  | 2.77 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.12 |  | C2/04/SC/01 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.3e-5 m3/s |  | 7052 Pa |  |  |  |  | 2.7 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.13 |  | C2/04/SC/02 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.3e-5 m3/s |  | 6653 Pa |  |  |  |  | 2.73 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.14 |  | C2/04/SC/03 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.3e-5 m3/s |  | 6314 Pa |  |  |  |  | 2.75 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.15 |  | C2/04/SC/04 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.3e-5 m3/s |  | 6025 Pa |  |  |  |  | 2.77 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.16 |  | C2/04/SC/05 | STAD* 15 |  | 15 (1/2") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 9e-5 m3/s |  | 5518 Pa |  |  |  |  | 2.93 turns |  |  | 52851-015 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.17 |  | C2/04/SC/06 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.2e-5 m3/s |  | 4693 Pa |  |  |  |  | 3.08 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.18 |  | C2/04/SC/07 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.2e-5 m3/s |  | 4329 Pa |  |  |  |  | 3.12 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.19 |  | C2/04/SC/08 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 4.3e-5 m3/s |  | 4144 Pa |  |  |  |  | 2.95 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.20 |  | C2/04/SC/09 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.2e-5 m3/s |  | 3300 Pa |  |  |  |  | 3.26 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.17.2.21 |  | C2/04/SC/10 | STAD* 10 |  | 10 (3/8") | Thread | Without drain |  | PN25; -20/120 °C | [7 empty] | 5.2e-5 m3/s |  | 3000 Pa |  |  |  |  | 3.32 turns |  |  | 52851-010 |  | 1 | [22 empty] | Hydraulic Network
| *A.18.1.1 |  | AHU/C2/05/01N | KTM 512 DN40/50 LF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.0012 m3/s |  |  |  |  | 15878 Pa |  | 5.4 turns |  |  | 52796-240&2*52759-040 |  | 1 | TA-Slider 500 Plus (5m) | Max. inlet pressure : 2.5e+6 Pa | Actuating time : 100; 200* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | 0(2)-10 V | Relay 220V | Fail-safe type : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 322225-10213 |  | 1 | Hydraulic Network
| *A.18.1.2 |  | AHU/C2/05/03N | KTM 512 DN25/32 LF | Ductile iron |  | Thread | PT 90 |  | PN25; -10/120 °C | [7 empty] | 0.00074 m3/s |  |  |  |  | 20868 Pa |  | 4.55 turns |  |  | 52796-225&2*52759-025 |  | 1 | TA-R25-F24 | Max. inlet pressure : 573885 Pa | Actuating time : 25 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0-10 V | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 44756-977 |  | 1 | Hydraulic Network
| *A.18.2 |  | AHU/C2/05/02N | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0041 m3/s |  |  |  |  | 22970 Pa |  | 9.44 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network
| *A.18.3 |  | AHU/C2/05/04N | KTM 512 DN65 LF | Ductile iron |  | Flange | PT 90 |  | PN16/25; -10/120 °C | [7 empty] | 0.0025 m3/s |  |  |  |  | 15947 Pa |  | 6.5 turns |  |  | 52791-765 |  | 1 | TA-MC 55Y | Max. inlet pressure : 2.302833e+6 Pa | Actuating time : 180; 100* s | IP auto(man.) : 54(30) | 24 VAC | 0(2)-10 V; 0(4)-20 mA | 0-10 V | No relay | Fail-safe type : No | Default return position : None | Max. Temp. : - | [8 empty] | 61055-003 |  | 1 | Hydraulic Network

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
322225-10213 |  |  | TA-Slider 500 Plus (5m); Actuating force = 500 N; Power Supply = 24 VAC; 24 VDC; Relay type = Relay 220V | 1
322226-10110 |  |  | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
322231-01391 |  |  | TA-Smart 125; Standard; Flange; PN 25; Kvs = 190; Qnom = 0.031 m3/s; Cable length to remote temp. sensor = 5 m | 2
44756-977 |  |  | TA-R25-F24; Actuating force = 125 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 6
50358-020 |  |  | TA-NV24; Actuating force = 800 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
52182-032 |  |  | STAF-SG 32; Standard; Flange; PN 16/25 | 1
52182-040 |  |  | STAF-SG 40; Standard; Flange; PN 16/25 | 2
52186-065 |  |  | STAF* 65; Standard; Flange; PN 16 | 1
52186-080 |  |  | STAF* 80; Standard; Flange; PN 16 | 1
52186-090 |  |  | STAF* 100; Standard; Flange; PN 16 | 1
52186-091 |  |  | STAF* 125; Standard; Flange; PN 16 | 1
52186-092 |  |  | STAF* 150; Standard; Flange; PN 16 | 1
52265-020 |  |  | STAP 20; [10000-60000] Pa; Standard; Thread; PN 16 | 1
52265-032 |  |  | STAP 32; [20000-80000] Pa; Standard; Thread; PN 16 | 1
52265-040 |  |  | STAP 40; [20000-80000] Pa; Standard; Thread; PN 16 | 8
52265-050 |  |  | STAP 50; [20000-80000] Pa; Standard; Thread; PN 16 | 2
52265-080 |  |  | STAP 80; [20000-80000] Pa; Standard; Flange; PN 16 | 1
52265-165 |  |  | STAP 65; [40000-160000] Pa; Standard; Flange; PN 16 | 1
52265-190 |  |  | STAP 100; [40000-160000] Pa; Standard; Flange; PN 16 | 1
52757-031 |  |  | Adapter 03; Adapter for TA-R25 actuator | 6
52757-901 |  |  | Adapter 01; Adapter for TA-NV24 and Belimo NV24 MFT + UNV 003 actuator | 1
52757-905 |  |  | Adapter 05; Adapter for TA-MC55 actuator | 7
52757-907 |  |  | Adapter 07; Adapter for TA-Slider 750/1250, TA-MC 100 actuators | 1
52759-025 |  |  | Conn. Piece: Thread, 25 (1") | 4
52759-032 |  |  | Conn. Piece: Thread, 32 (1 1/4") | 2
52759-040 |  |  | Conn. Piece: Thread, 40 (1 1/2") | 8
52759-140 |  |  | Conn. Piece: Thread male, 40 (1 1/2") | 2
52791-490 |  |  | KTM 512 DN100 LF; PT 90; Flange | 1
52791-590 |  |  | KTM 512 DN100 NF; PT 90; Flange | 1
52791-765 |  |  | KTM 512 DN65 LF; PT 90; Flange | 6
52791-865 |  |  | KTM 512 DN65 NF; PT 90; Flange | 1
52795-225 |  |  | DA 516 DN25/32; [10000-100000] Pa; PT 90; Thread; PN 25 | 1
52796-040 |  |  | KTM 512 DN40/50 NF; PT 90; Thread | 2
52796-040 |  |  | KTM 512 DN40/50 NF; PT 90; Thread male | 1
52796-225 |  |  | KTM 512 DN25/32 LF; PT 90; Thread | 2
52796-240 |  |  | KTM 512 DN40/50 LF; PT 90; Thread | 2
52851-010 |  |  | STAD* 10; Without drain; Thread; PN 25 | 153
52851-015 |  |  | STAD* 15; Without drain; Thread; PN 25 | 70
52851-020 |  |  | STAD* 20; Without drain; Thread; PN 25 | 27
52851-025 |  |  | STAD* 25; Without drain; Thread; PN 25 | 3
52851-050 |  |  | STAD* 50; Without drain; Thread; PN 25 | 2
52851-620 |  |  | STAD* 20; With drain 3/4"; Thread; PN 25 | 1
52851-632 |  |  | STAD* 32; With drain 3/4"; Thread; PN 25 | 1
52851-640 |  |  | STAD* 40; With drain 3/4"; Thread; PN 25 | 6
52851-650 |  |  | STAD* 50; With drain 3/4"; Thread; PN 25 | 2
61055-003 |  |  | TA-MC 55Y; Actuating force = 600 N; Power Supply = 24 VAC; Relay type = No relay | 7