## Valves export (1)
Technical informations | #1 | #2 | Primary product | [26 empty] | Secondary product | [21 empty] | Selection mode
|  |  | Product | [13 empty] | Technical informations | [9 empty] | Article N° | Local Art. Nr. | Qty | Product | [14 empty] | Technical informations |  |  |  | Article N° | Local Art. Nr. | Qty
|  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Location | Kvs | Qnom | Cable length to remote temp. sensor | Power Supply | Input | Output signal | Flow | Power/DT | Dp | Control mode | Dpl | Dp min. | Dp max. | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [9 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
| A1_1-3 |  | TA-Compact-P 20 | Ametal(tm) |  | Thread male | Standard |  | PN16; -10/90 °C | [7 empty] | 0.00031 m3/s | 25000 W / 20 °C |  |  |  | 14964 Pa |  | pos. 9.25 |  |  | 52164-020 |  | 3 | EMO T 230/NC (0.8m) | Close-off Dp : 400000 Pa | Actuating time : 120 s | IP auto(man.) : 54 | 230 VAC | On-off | - | No relay | Fail-safe type : No | Default return position : Extending | [9 empty] | 1833-00.500 |  | 3 | Individual selection
| A2_1-5 |  | TA-Compact-P 20 | Ametal(tm) |  | Thread male | Standard |  | PN16; -10/90 °C | [7 empty] | 0.00031 m3/s | 25000 W / 20 °C |  |  |  | 14964 Pa |  | pos. 9.25 |  |  | 52164-020 |  | 5 | EMO T 24/NC (0.8m) | Close-off Dp : 400000 Pa | Actuating time : 120 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Extending | [9 empty] | 1843-00.500 |  | 5 | Individual selection
| *A.1 | A2_5_Air Curtain | TA-Compact-P 20 | Ametal(tm) |  | Thread male | Standard |  | PN16; -10/90 °C | [7 empty] | 0.00031 m3/s |  |  |  |  | 14978 Pa |  | pos. 9.5 |  |  | 52164-020 |  | 1 | EMO T 24/NC (0.8m) | Close-off Dp : 400000 Pa | Actuating time : 120 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Extending | Max. Temp. : 120°C | [8 empty] | 1843-00.500 |  | 1 | Hydraulic Network
| *A.2.1 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19509 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.2 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19492 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.3 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19477 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.4 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19465 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.5 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19454 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.6 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19446 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.7 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19440 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.8 | Konv5._1200 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19437 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.9 | Konv4._1200 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19435 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.10 | Konv3._1000 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19435 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.11 | Konv2._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19435 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network
| *A.2.12 | Konv1._2500 | V-exact II 10(3/8") | Gunmetal nickel-plated |  | Rad. union/Thread | Straight |  | PN10; -10/120 °C | [7 empty] | 5.984e-6 m3/s |  | 19437 Pa |  |  |  |  | Setting = 1 |  |  | 3712-01.000 |  | 1 | EMO T 24/NO (0.8m) |  | Actuating time : 30 s/mm | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off | - | No relay | Fail-safe type : No | Default return position : Retracting | Max. Temp. : 120°C | [8 empty] | 1847-00.500 |  | 1 | Hydraulic Network

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
1833-00.500 |  |  | EMO T 230/NC (0.8m); Actuating force = 125 N; Power Supply = 230 VAC; Relay type = No relay | 3
1843-00.500 |  |  | EMO T 24/NC (0.8m); Actuating force = 125 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 6
1847-00.500 |  |  | EMO T 24/NO (0.8m); Actuating force = 125 N; 24 VAC; 24 VDC | 12
3712-01.000 |  |  | V-exact II 10(3/8"); Straight; Thread | 12
52164-020 |  |  | TA-Compact-P 20; Standard; Thread male; PN 16 | 9