## Pneumatex export (1)
Pressurisation and Water Quality selection | [7 empty] | Pressurisation input data | [22 empty] | Pressurisation calculated data | [26 empty] | Separator tech. info |  |  |  | Safety valve tech. info | [6 empty] | Product parameters
| #1 | #2 | Qty | Product name | Product function | Article N° | Local Art. Nr. |  | Application type | Fluid type: | Norm | System volume [Vs] | Solar collector volume [Vkoll] | Solar collector multiplier factor | Storage tank volume [Vsto] | Storage tank max. temperature [Tmax,sto] | Installed power [Qs] | Static height [Hst] | Min. required equipment pressure [pz] | Safety valve response pressure [pSV] | Safety temperature limiter [TAZ] | Maximum temperature [tsmax] | Supply temperature | Return temperature | Minimum temperature [tsmin] | Fill temperature | Pressurisation on | Pump head | Max width | Max height | System expansion coefficient [e] | System expansion volume [Ve] | Factor [X] | System expansion volume [e.Vs.X] | Storage tank expansion coefficient [esto] | Storage tank expansion volume [Vsto.esto] | Total expansion volume [Ve,tot] | Solar collector security volume [VDK] | Min. water reserve (To add for expansion) [Vwr,min] | Degassing water reserve [Vv] | Vessel net volume [Vn] | Min. water reserve (Included in expansion) [Vwr,min] | Water reserve [Vwr] | Contracted volume [Vcontr] | Vapour over-pressure [pv] | Minimum pressure [p0] | Min. initial pressure [pa,min] | Initial pressure [pa] | Filling pressure [pfill] | Target pressure [pman] | Final pressure [pe] | Specific flowrate of equalization volume [qN/Q] | Necessary flowrate of equalization volume [qN] | Pressure factor [PF] | Required nominal volume | Expansion pipe up to (10 m) [DNe] | Expansion pipe up to (30 m) [DNe] |  | Flow | Power/DT | Dp |  | Set pressure | Heat generator type | Power 100% | Power | Max. collector | Collector
[9 empty] | - | - | - | m3 | m3 | - | m3 | °C | W | m | Pa | Pa | °C | °C | °C | °C | °C | °C | - | Pa | m | m | - | m3 | - | m3 | - | m3 | m3 | m3 | m3 | m3 | m3 | m3 | m3 | m3 | Pa | Pa | Pa | Pa | Pa | Pa | Pa | m3/s/W | m3/s | - | m3 | - | - |  | m3/s | W/°C | Pa |  | Pa | - | W | W | m2 | m2
Pressurisation
Individual selection
| 5 | first | [6 empty] | Cooling | Water |  | 5 m3 | - | - | - | - | 0 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.049 m3 | - | - | - | - | 0.049 m3 | - | 0.025 m3 | - | 0.074 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 168080 Pa | 188080 Pa | 1.0667e-10 m3/s/W | 0 m3/s | 1.10 | 0.081 m3 | 32 (1 1/4") | 40 (1 1/2")
|  |  | 4 | TV 4.1 EH | TecBox - Transfero/Degassing/Pump | 811 1510 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 4 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 4 | DH 15 | Push button valve for shut-off of manometers | 500 1060
|  |  | 4 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 236 kg
|  |  | 4 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 3 | second | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | - | 0.044 m3 | - | 0.024 m3 | 0.0003 m3 | 0 Pa | 118080 Pa | - | 162353 Pa | 163032 Pa | - | 250000 Pa | - | - | 2.65 | 0.117 m3 | - | -
|  |  | 2 | SU 140.3 | Statico | 710 1008 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.14 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 26 kg | Max. weight = 166 kg
|  |  | 2 | DLV 20 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 746 2000
|  |  | 2 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 3 | third | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | - | 0.044 m3 | - | 0.024 m3 | 0.0003 m3 | 0 Pa | 118080 Pa | - | 162353 Pa | 163032 Pa | - | 250000 Pa | - | - | 2.65 | 0.117 m3 | - | -
|  |  | 2 | SQ 140.6 | Membrane vessel | ****** *****(deleted) | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.14 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 25 kg | Max. weight = 165 kg
|  |  | 2 | DLV 25 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 301010-50601
|  |  | 2 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 3 | fourth | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | - | 0.044 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 158080 Pa | 168080 Pa | 1.0667e-10 m3/s/W | 6.4e-6 m3/s | 1.10 | 0.049 m3 | 20 (3/4") | 20 (3/4")
|  |  | 3 | Simply Compresso C 2.1-80 S | TecBox - Compresso/Compressor | 301021 41001 | [63 empty] | PS = 600000 Pa | Power = 300 W | Supply voltage = 230 VAC
|  |  | 3 | CD 80.9 | Integrated vessel | - | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 900000 Pa | Temp. range = 5/70 °C | Weight = 16 kg | Max. weight = 96 kg
|  |  | 3 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 6 | fifth | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | - | 0.044 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 168080 Pa | 188080 Pa | 1.0667e-10 m3/s/W | 6.4e-6 m3/s | 1.10 | 0.049 m3 | 32 (1 1/4") | 40 (1 1/2")
|  |  | 3 | TV 4.1 EH | TecBox - Transfero/Degassing/Pump | 811 1510 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 3 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 3 | DH 15 | Push button valve for shut-off of manometers | 500 1060
|  |  | 3 | Manometer H | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 501 1037
|  |  | 3 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 236 kg
|  |  | 3 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 3 | sixth | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | - | 0.044 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 158080 Pa | 168080 Pa | 1.0667e-10 m3/s/W | 6.4e-6 m3/s | 1.10 | 0.049 m3 | 20 (3/4") | 20 (3/4")
|  |  | 3 | C 10.1-3.0 Connect | TecBox - Compresso/Compressor | 810 1420 | [63 empty] | PS = 300000 Pa | Power = 600 W | Supply voltage = 230 VAC
|  |  | 3 | CU 200.6 | Primary vessel | 712 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 234 kg
|  |  | 3 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
| 7 | seventh | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | 0.002 m3 | 0.046 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 168080 Pa | 188080 Pa | 1.0667e-10 m3/s/W | 6.4e-6 m3/s | 1.10 | 0.051 m3 | 32 (1 1/4") | 40 (1 1/2")
|  |  | 3 | TV 4.1 EH | TecBox - Transfero/Degassing/Pump | 811 1510 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 3 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 3 | DH 15 | Push button valve for shut-off of manometers | 500 1060
|  |  | 3 | DLV 20 | Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 535 1434
|  |  | 3 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 236 kg
|  |  | 3 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
|  |  | 3 | P AB5 | TecBox - Pleno/Make-up water | 813 3320 | [63 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
| 5 | eighth | [6 empty] | Cooling | Water |  | 3 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | 0 °C |  | pump suction | - | 0 m | 0 m | 0.00971 | 0.029 m3 | - | - | - | - | 0.029 m3 | - | 0.015 m3 | 0.002 m3 | 0.046 m3 | - | - | - | 0 Pa | 118080 Pa | - | 148080 Pa |  | 158080 Pa | 168080 Pa | 1.0667e-10 m3/s/W | 6.4e-6 m3/s | 1.10 | 0.051 m3 | 20 (3/4") | 20 (3/4")
|  |  | 2 | C 10.1-3.0 Connect | TecBox - Compresso/Compressor | 810 1420 | [63 empty] | PS = 300000 Pa | Power = 600 W | Supply voltage = 230 VAC
|  |  | 2 | CU 200.6 | Primary vessel | 712 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 234 kg
|  |  | 2 | DD 8.10 | Intermediate vessel | 714 2020 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3.9 kg | Max. weight = 11.9 kg
|  |  | 2 | V 2.1 F | TecBox - Vento/Degassing | *** ****(deleted) | [63 empty] | PS = 600000 Pa | Power = 600 W | Supply voltage = 230 VAC
|  |  | 2 | P | TecBox - Pleno/Make-up water | *** ****(deleted) | [63 empty] | PS = 1e+6 Pa | Power = 20 W | Supply voltage = 230 VAC
|  |  | 2 | V 4.1 E Connect | TecBox - Vento/Degassing | 812 1101 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 2 | P AB5 | TecBox - Pleno/Make-up water | 813 3320 | [63 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
[9 empty] | Cooling | Water/Ethylene Glycol - 30% by weight |  | 5 m3 | - | - | - | - | 0 W | 0 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | -14.6 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.0251 | 0.126 m3 | - | - | - | - | 0.126 m3 | - | 0.025 m3 | 0.002 m3 | 0.153 m3 | - | 0.098 m3 | 0.042 m3 | 0 Pa | 20000 Pa | - | 79585 Pa | 126714 Pa | - | 250000 Pa | - | - | 1.52 | 0.232 m3 | - | -
|  |  | 2 | SU 300.3 | Statico | 710 1011 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.3 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 37 kg | Max. weight = 353 kg
|  |  | 2 | DLV 20 | Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 535 1434
|  |  | 2 | DD 25.10 | Intermediate vessel | 714 2023 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.025 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 8.1 kg | Max. weight = 34.4 kg
|  |  | 2 | PI | TecBox - Pleno/Make-up water | *** ****(deleted) | [63 empty] | PS = 1e+6 Pa | Power = 40 W | Supply voltage = 230 VAC
| nineth | with pleno&refill | [6 empty] | Solar | Water |  | 0.166 m3 | - | - | - | - | 0 W | 10 m | - | 300000 Pa | 100 °C | - | 70 °C | 50 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.0228 | 0.0038 m3 | - | - | - | - | 0.0038 m3 | 0.018 m3 | 0.003 m3 | - | 0.024 m3 | - | 0.026 m3 | - | 0 Pa | 118100 Pa | - | 225294 Pa | 225596 Pa | - | 250000 Pa | - | - | 2.65 | 0.065 m3 | - | -
|  |  | 3 | SD 80.3 | Statico | 710 1006 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 12.7 kg | Max. weight = 92.7 kg
|  |  | 3 | PI | TecBox - Pleno/Make-up water | *** ****(deleted) | [63 empty] | PS = 1e+6 Pa | Power = 40 W | Supply voltage = 230 VAC
|  |  | 3 | Refill Demin 4000 | Pleno Refill Desalination | 813 3016 | [63 empty] | Capacity = 0.713 m3/mol/m3 | Heigth = 0.571 m | Weight = 7.8 kg
|  |  | 3 | Electronic water meter | Electronic water meter with countdown function for manual make up. | 813 3121
|  |  | 3 | Total hardness measuring | Total hardness measuring equipment for app. 100 measurements. | 813 3120
| tenth | soft | [6 empty] | Solar | Water |  | 0.166 m3 | - | - | - | - | 600000 W | 10 m | - | 600000 Pa | 100 °C | - | 70 °C | 50 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.0228 | 0.0038 m3 | - | - | - | - | 0.0038 m3 | 0.018 m3 | 0.003 m3 | - | 0.024 m3 | - | 0.029 m3 | - | 0 Pa | 118100 Pa | - | 423642 Pa | 424898 Pa | - | 540000 Pa | - | - | 1.52 | 0.037 m3 | - | -
|  |  | 2 | SD 50.10 | Statico | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 2 | DLV 20 | Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 535 1434
|  |  | 2 | PI | TecBox - Pleno/Make-up water | *** ****(deleted) | [63 empty] | PS = 1e+6 Pa | Power = 40 W | Supply voltage = 230 VAC
|  |  | 2 | Refill 6000 Filter | Pleno Refill Softening | *** ****(deleted) | [63 empty] | Capacity = 1.07 m3/mol/m3 | Heigth = 0.571 m | Weight = 4.1 kg
|  |  | 2 | Battery for WM | Internal battery for the electronic water meter equipment. | 813 3122
| eleventh | WT only | [6 empty] | Cooling | Water/Ethylene Glycol - 30% by weight |  | 5 m3 | - | - | - | - | 0 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | -14.6 °C |  | pump suction | - | 0 m | 0 m | 0.0251 | 0.126 m3 | - | - | - | - | 0.126 m3 | - | 0.025 m3 | 0.002 m3 | 0.153 m3 | - | - | - | 0 Pa | 123375 Pa | - | 153375 Pa |  | 173375 Pa | 193375 Pa | 1.0667e-10 m3/s/W | 0 m3/s | 1.10 | 0.168 m3 | 32 (1 1/4") | 40 (1 1/2")
|  |  | 3 | TV 4.1 EH | TecBox - Transfero/Degassing/Pump | 811 1510 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 3 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 64.7 kg
|  |  | 3 | Manometer H | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 501 1037
|  |  | 3 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 247 kg
|  |  | 3 | DD 25.10 | Intermediate vessel | 714 2023 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.025 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 8.1 kg | Max. weight = 34.4 kg
|  |  | 3 | Refill Demin 18000 | Pleno Refill Desalination | 813 3270 | [63 empty] | Capacity = 3.21 m3/mol/m3 | Heigth = 0.458 m | Weight = 15.7 kg
|  |  | 3 | Total hardness measuring | Total hardness measuring equipment for app. 100 measurements. | 813 3120
| twelveth | comb | [6 empty] | Cooling | Water/Ethylene Glycol - 30% by weight |  | 5 m3 | - | - | - | - | 0 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | -14.6 °C |  | pump suction | - | 0 m | 0 m | 0.0251 | 0.126 m3 | - | - | - | - | 0.126 m3 | - | 0.025 m3 | 0.002 m3 | 0.153 m3 | - | - | - | 0 Pa | 123375 Pa | - | 153375 Pa |  | 173375 Pa | 193375 Pa | 1.0667e-10 m3/s/W | 0 m3/s | 1.10 | 0.168 m3 | 32 (1 1/4") | 40 (1 1/2")
|  |  | 2 | TV 4.1 EH | TecBox - Transfero/Degassing/Pump | 811 1510 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 2 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 64.7 kg
|  |  | 2 | Manometer H | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 501 1037
|  |  | 2 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 247 kg
|  |  | 2 | DD 25.10 | Intermediate vessel | 714 2023 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.025 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 8.1 kg | Max. weight = 34.4 kg
|  |  | 2 | P AB5 R | TecBox - Pleno/Make-up water | 813 3330 | [63 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
|  |  | 2 | Refill Demin 18000 | Pleno Refill Desalination | 813 3270 | [63 empty] | Capacity = 3.21 m3/mol/m3 | Heigth = 0.458 m | Weight = 15.7 kg
| thirteenth | compr & refill | [6 empty] | Cooling | Water/Ethylene Glycol - 30% by weight |  | 5 m3 | - | - | - | - | 0 W | 10 m | - | 300000 Pa | - | 45 °C | 6 °C | 12 °C | -14.6 °C |  | pump suction | - | 0 m | 0 m | 0.0251 | 0.126 m3 | - | - | - | - | 0.126 m3 | - | 0.025 m3 | 0.002 m3 | 0.153 m3 | - | - | - | 0 Pa | 123375 Pa | - | 153375 Pa |  | 163375 Pa | 173375 Pa | 1.0667e-10 m3/s/W | 0 m3/s | 1.10 | 0.168 m3 | 20 (3/4") | 20 (3/4")
|  |  | 1 | C 10.1-3.0 Connect | TecBox - Compresso/Compressor | 810 1420 | [63 empty] | PS = 300000 Pa | Power = 600 W | Supply voltage = 230 VAC
|  |  | 1 | CU 200.6 | Primary vessel | 712 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 245 kg
|  |  | 1 | DD 25.10 | Intermediate vessel | 714 2023 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.025 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 8.1 kg | Max. weight = 34.4 kg
|  |  | 1 | P RC | TecBox - Pleno/Make-up water | *** ****(deleted) | [63 empty] | PS = 1e+6 Pa | Power = 20 W | Supply voltage = 230 VAC
|  |  | 1 | Refill Demin 2000 | Pleno Refill Desalination | 813 3015 | [63 empty] | Capacity = 0.357 m3/mol/m3 | Heigth = 0.571 m | Weight = 4.1 kg
| fourteenth | no pleno refill
|  |  | 3 | P AB5 R | TecBox - Pleno/Make-up water | 813 3330 | [63 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
|  |  | 3 | Refill Demin 18000 | Pleno Refill Desalination | 813 3270 | [63 empty] | Capacity = 3.21 m3/mol/m3 | Heigth = 0.458 m | Weight = 15.7 kg
|  |  | 3 | Electronic water meter | Electronic water meter with countdown function for manual make up. | 813 3121
| heat | no norm | [6 empty] | Heating | Water | None | 5 m3 | - | - | - | - | 100000 W | 10 m | - | 300000 Pa | 100 °C | - | 70 °C | 50 °C | 5 °C |  | pump suction | - | 0 m | 0 m | 0.0228 | 0.114 m3 | - | - | - | - | 0.114 m3 | - | 0.025 m3 | - | 0.139 m3 | - | - | - | 0 Pa | 118100 Pa | - | 148100 Pa |  | 158100 Pa | 168100 Pa | 1.3889e-10 m3/s/W | 1.389e-5 m3/s | 1.10 | 0.153 m3 | - | -
|  |  | 1 | Simply Compresso C 2.1-80 S | TecBox - Compresso/Compressor | 301021 41001 | [63 empty] | PS = 600000 Pa | Power = 300 W | Supply voltage = 230 VAC
|  |  | 1 | CD 80.9 | Integrated vessel | - | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 900000 Pa | Temp. range = 5/70 °C | Weight = 16 kg | Max. weight = 96 kg
|  |  | 1 | CD 80.9 E | Integrated vessel | 301021 41003 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 16 kg | Max. weight = 96 kg
| heat | swki norm | [6 empty] | Heating | Water | SWKI/SICC/SITC HE301-01 | 5 m3 | - | - | - | - | 100000 W | 10 m | - | 300000 Pa | 100 °C | - | 70 °C | 50 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0.0171 | - | 2.04 | 0.174 m3 | - | - | 0.174 m3 | - | - | - | 0.174 m3 | 0.088 m3 | 0.119 m3 | - | 0 Pa | 128100 Pa | - | 172025 Pa | 185388 Pa | - | 230769 Pa | - | - | 3.22 | 0.56 m3 | - | -
|  |  | 1 | SQ 600.6 | Membrane vessel | ****** *****(deleted) | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.6 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 76 kg | Max. weight = 676 kg
| Vessel in parallele | [7 empty] | Heating | Water | EN 12828 | 5 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | 100 °C | - | 90 °C | 80 °C | 5 °C | 15 °C | pump suction | - | 0 m | 0 m | 0.0360 | 0.18 m3 | - | - | - | - | 0.18 m3 | - | 0.025 m3 | - | 0.205 m3 | - | 0.122 m3 | - | 0 Pa | 118100 Pa | 148100 Pa | 157250 Pa | 158994 Pa | - | 250000 Pa | - | - | 2.65 | 0.543 m3 | - | -
|  |  | 4 | SU 200.3 | Statico | 710 1010 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.2 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 30 kg | Max. weight = 230 kg
|  |  | 8 | DLV 20 | Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 535 1434
|  |  | 3 | DD 12.10 | Intermediate vessel | 714 2021 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.012 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 5.1 kg | Max. weight = 17.1 kg
| SQ parallele | [7 empty] | Heating | Water | EN 12828 | 5 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | 100 °C | - | 90 °C | 80 °C | 5 °C | 15 °C | pump suction | - | 0 m | 0 m | 0.0360 | 0.18 m3 | - | - | - | - | 0.18 m3 | - | 0.025 m3 | - | 0.205 m3 | - | 0.159 m3 | - | 0 Pa | 118100 Pa | 148100 Pa | 165054 Pa | 166699 Pa | - | 250000 Pa | - | - | 2.65 | 0.543 m3 | - | -
|  |  | 3 | SQ 300.6 | Membrane vessel | ****** *****(deleted) | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.3 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 39 kg | Max. weight = 339 kg
|  |  | 3 | DLV 25 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 301010-50601
|  |  | 2 | DD 25.10 | Intermediate vessel | 714 2023 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.025 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 8.1 kg | Max. weight = 33.1 kg
| cprssor parallele + sec | 2 tecbox | [6 empty] | Heating | Water | EN 12828 | 5 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | 100 °C | - | 90 °C | 80 °C | 5 °C |  | pump suction | - | 0 m | 0 m | 0.0360 | 0.18 m3 | - | - | - | - | 0.18 m3 | - | 0.025 m3 | - | 0.205 m3 | - | - | - | 0 Pa | 118100 Pa | - | 148100 Pa |  | 158100 Pa | 168100 Pa | 1.7111e-10 m3/s/W | 1.027e-5 m3/s | 1.10 | 0.225 m3 | 20 (3/4") | 20 (3/4")
|  |  | 2 | C 10.2-3.0 Connect | TecBox - Compresso/Compressor | 810 1460 | [63 empty] | PS = 300000 Pa | Power = 1200 W | Supply voltage = 230 VAC
|  |  | 1 | CU 200.6 | Primary vessel | 712 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 234 kg
|  |  | 1 | CU 200.6 E | Secondary vessel | 712 2000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 234 kg
|  |  | 2 | DD 18.10 | Intermediate vessel | 714 2022 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.018 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 6.3 kg | Max. weight = 24.3 kg
| trans parallel + sec | 2 tecbox | [6 empty] | Heating | Water | EN 12828 | 5 m3 | - | - | - | - | 60000 W | 10 m | - | 300000 Pa | 100 °C | - | 90 °C | 80 °C | 5 °C |  | pump suction | - | 0 m | 0 m | 0.0360 | 0.18 m3 | - | - | - | - | 0.18 m3 | - | 0.025 m3 | - | 0.205 m3 | - | - | - | 0 Pa | 118100 Pa | - | 148100 Pa |  | 168100 Pa | 188100 Pa | 1.7111e-10 m3/s/W | 1.027e-5 m3/s | 1.10 | 0.225 m3 | 50 (2") | 65 (2 1/2")
|  |  | 2 | TV 6.2 EH | TecBox - Transfero/Degassing/Pump | 811 1521 | [63 empty] | PS = 1e+6 Pa | Power = 2200 W | Supply voltage = 230 VAC
|  |  | 2 | SD 50.10 | Buffer vessel | 710 3005 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 5 | DLV 20 | Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 535 1434
|  |  | 1 | TU 200 | Primary vessel | 713 1000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 236 kg
|  |  | 1 | TU 200 E | Secondary vessel | 713 2000 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.2 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 36 kg | Max. weight = 236 kg
|  |  | 2 | DD 18.10 | Intermediate vessel | 714 2022 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.018 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 6.3 kg | Max. weight = 24.3 kg
Direct selection
| Dir sel | Expansion Vessel Membrane
|  |  | 4 | SQ 400.6 |  | ****** *****(deleted) | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.4 m3 | PS = 600000 Pa | Temp. range = 5/70 °C | Weight = 57 kg | Max. weight = 457 kg
|  |  | 4 | DLV 25 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 301010-50601
| Dir sel | vessel membr
|  |  | 1 | MN-80 |  | ***** ******(deleted) | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 600000 Pa | Temp. range = -10/100 °C | Weight = 12.4 kg | Max. weight = 92.4 kg
|  |  | 1 | Manometer H | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 501 1037
| Dir sel | primary vessel
|  |  | 1 | CD 80.9 |  | - | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.08 m3 | PS = 900000 Pa | Temp. range = 5/70 °C | Weight = 16 kg | Max. weight = 96 kg
| Dir sel | secondary vessel
|  |  | 1 | TU 500 E |  | 713 2003 | [63 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0.5 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 71 kg | Max. weight = 571 kg
| Dir sel | Intermediate vessel
|  |  | 1 | DU 500.6 |  | 714 1006 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.5 m3 | PS = 600000 Pa | Temp. range = -10/110 °C | Weight = 61 kg | Max. weight = 561 kg
| Dir sel | Aquapresso
|  |  | 1 | AU 400.10 |  | 711 1010 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.4 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 71 kg | Max. weight = 471 kg
| Dir sel | Transfero ti
|  |  | 1 | TI 90.2 PC1 |  | *** ****(deleted) | [63 empty] | PS = 1.6e+6 Pa | Power = 3000 W | Supply voltage = 3x400 VAC
| Dir sel | vento connect
|  |  | 1 | V 8.1 EC Connect |  | 812 1203 | [63 empty] | PS = 1e+6 Pa | Power = 1400 W | Supply voltage = 230 VAC
| Dir sel | pleno pi
|  |  | 1 | PI 6.2 |  | *** ****(deleted) | [63 empty] | PS = 800000 Pa | Power = 1100 W | Supply voltage = 230 VAC
| Dir sel | refill
|  |  | 3 | Refill Demin 4000 |  | 813 3016 | [63 empty] | Capacity = 0.713 m3/mol/m3 | Heigth = 0.571 m | Weight = 7.8 kg
|  |  | 3 | Electronic water meter | Electronic water meter with countdown function for manual make up. | 813 3121
|  |  | 3 | Key for filter | Key to change filter and cartridges. | 813 3112
| Dir sel | tecbox with buffer
|  |  | 2 | TV 4.1 E |  | 811 1500 | [63 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 2 | SU 140.10 | Buffer vessel | 710 3007 | [63 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0.14 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 34 kg | Max. weight = 174 kg
|  |  | 2 | Thermometer/Manometer TH | Pressure display range 0-4 bar, temperature display range 0-120 °C, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Rear connection. | 501 1038
Air vents & separators
Individual selection
[10 empty] | Water/Ethylene Glycol - 30% by weight Temperature: 6 °C | [48 empty] | 0.002 m3/s |  | 2846 Pa
|  |  | 2 | ZG 65 | Cyclonic dirt separator | 303041-11000 | [63 empty] | Connection = Flange | Version = Standard | PN 16; -10/110 °C
|  |  | 2 | ZGI 65 | Zeparo G-Force Insulation ZGI | 30305141000
|  |  | 2 | ZUTX 25 | Zeparo G-Force Air Vent ZUTX | 789 1325
[10 empty] | Water/Ethylene Glycol - 30% by weight Temperature: 6 °C | [48 empty] | 0.002 m3/s |  | 972 Pa
|  |  | 1 | ZIO 50F | Micro-bubble or dirt separator | 788 2050 | [63 empty] | Connection = Flange | Version = Industrial | PN 10; -10/110 °C
|  |  | 1 | ZHI-ZIO 50-65 | Thermal insulation (Rockwool 2 part galvanized steel cladding) for Zeparo ZIO | 787 2065
[10 empty] | Water/Ethylene Glycol - 30% by weight Temperature: 6 °C | [48 empty] | 0.002 m3/s |  | 2546 Pa
|  |  | 1 | ZUD 40 | Dirt separator | 789 2140 | [63 empty] | Connection = Thread | Version = Standard | PN 10; -10/110 °C
|  |  | 1 | ZHU-ZUD/ZUM 40 | Thermal insulation (EPP) for Zeparo ZHU-ZUD/ZUM | 787 1440
[10 empty] | Water/Ethylene Glycol - 30% by weight Temperature: 6 °C | [48 empty] | 0.002 m3/s |  | 2546 Pa
|  |  | 1 | ZUK 40 | Micro-bubble & dirt separator | *** ****(deleted) | [63 empty] | Connection = Thread | Version = Standard | PN 10; -10/110 °C
|  |  | 1 | ZHU-ZUK/ZUKM 40 | Thermal insulation (EPP) for Zeparo ZUK/ZUKM | 787 1340
Direct selection
| Dir sel | air vent ZUT
|  |  | 2 | ZUTS 15 |  | 789 1615 | [63 empty] | Dpp = 1e+6 Pa | Connection = Thread | Version = Solar | PN 10; -10/160 °C
| Dir sel | Air vent ZUP
|  |  | 1 | ZUPW 10 |  | *** ****(deleted) | [63 empty] | Dpp = 1e+6 Pa | Connection = Thread male | Version = Purge, white | PN 10; -10/110 °C
| Dir sel | Sep cyclonic dirt ZG
|  |  | 3 | ZG 80 W | Cyclonic dirt separator | 303041-21100 | [63 empty] | Connection = Welding and Groove | Version = Standard | PN 16; -10/110 °C
|  |  | 3 | ZGM 65-100 | Zeparo G-Force Magnet ZGM | 303051-11000
| Dir sel | Micro bubble sep
|  |  | 1 | ZUVS 40 | Micro-bubble separator | 789 1740 | [63 empty] | Connection = Thread | Version = Solar | PN 10; -10/160 °C
| Dir sel | Dirt sep
|  |  | 3 | ZUD 40 | Dirt separator | 789 2140 | [63 empty] | Connection = Thread | Version = Standard | PN 10; -10/110 °C
|  |  | 3 | ZHU-ZUD/ZUM 40 | Thermal insulation (EPP) for Zeparo ZHU-ZUD/ZUM | 787 1440
| Dir sel | Micro bubble & dirt
|  |  | 1 | ZUKM 25 | Micro-bubble & dirt separator | 789 4225 | [63 empty] | Connection = Thread | Version = Magnetic | PN 10; -10/110 °C
| Dir sel | micro buble Or dirt
|  |  | 1 | ZIO 100F | Micro-bubble or dirt separator | 788 2100 | [63 empty] | Connection = Flange | Version = Industrial | PN 10; -10/110 °C
|  |  | 1 | ZHI-ZIO 80-100 | Thermal insulation (Rockwool 2 part galvanized steel cladding) for Zeparo ZIO | 787 2100
Safety valves & accessories
Individual selection
[10 empty] | Hot water(-10 / 120 °C) | [52 empty] | 200000 Pa | Heating, Direct | 68000 W | 1500 W
|  |  | 1 | DSV 15-2.0 DGH | Safety valve | 536 1020 | [63 empty] | Size = 15 (1/2") | Connection (in / out ) = Thread (G 1/2" / G 1")
[10 empty] | Hot water(-10 / 120 °C) | [52 empty] | 200000 Pa | Heating, Direct | 68000 W | 1500 W
|  |  | 1 | DSV 15-2.0 DGH | Safety valve | 536 1020 | [63 empty] | Size = 15 (1/2") | Connection (in / out ) = Thread (G 1/2" / G 1")
[10 empty] | Water, water-glycol mixture(-50 / 120 °C) | [52 empty] | 300000 Pa |  | 4.4e+6 W | 1500 W
|  |  | 1 | DSV 20-3.0 F | Safety valve | 301051-20530 | [63 empty] | Size = 20 (3/4") | Connection (in / out ) = Thread (G 3/4" / G 3/4")
[10 empty] | Solar hot water or mixture(-10 / 160 °C) | [52 empty] | 300000 Pa |  | 100000 W | 1600 W | 100 m2 | 10 m2
|  |  | 1 | DSV 20-3.0 SOL | Safety valve | 301051-10530 | [63 empty] | Size = 20 (3/4") | Connection (in / out ) = Thread (G 3/4" / G 1")
Direct selection
| Dir sel | Safety valve H | [7 empty] | Hot water(-10 / 120 °C)
|  |  | 1 | DSV 40-2.5 DGH | Safety valve | *** ****(deleted) | [63 empty] | Size = 40 (1 1/2") | Connection (in / out ) = Flange (DN40 / DN65)
| Dir sel | Safety valve C | [7 empty] | Water, water-glycol mixture(-50 / 120 °C)
|  |  | 1 | DSV 40-4.0 F | Safety valve | 301051-20840 | [63 empty] | Size = 40 (1 1/2") | Connection (in / out ) = Thread (G 1 1/2" / G 1 1/2")
| Dir sel | Safety valve S | [7 empty] | Solar hot water or mixture(-10 / 160 °C)
|  |  | 1 | DSV 20-8.0 SOL | Safety valve | 301051-10580 | [63 empty] | Size = 20 (3/4") | Connection (in / out ) = Thread (G 3/4" / G 1")

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*** **** (deleted) |  |  | DSV 40-2.5 DGH; Bellows; Flange; PN 16 | 1
*** **** (deleted) |  |  | PI 6.2 (Make-up water); PN 6 | 1
*** **** (deleted) |  |  | TI 90.2 PC1 (Pump); PN 16 | 1
*** **** (deleted) |  |  | ZUPW 10; Purge, white; Thread male; PN 10 | 1
*** **** (deleted) |  |  | ZUK 40; Standard; Thread; PN 10 | 1
***** ****** (deleted) |  |  | MN-80 (Membrane vessel); Standard; PN 6 | 1
| 501 1037 |  | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 1
****** ***** (deleted) |  |  | SQ 400.6 (Membrane vessel); Standard; PN 6 | 4
| 301010-50601 |  | DLV 25 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 4
****** ***** (deleted) |  |  | SQ 300.6 (Membrane vessel); Standard; PN 6 | 3
| 301010-50601 |  | DLV 25 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 3
714 2023 |  |  | DD 25.10 (Intermediate vessel); Standard; PN 10 | 2
****** ***** (deleted) |  |  | SQ 600.6 (Membrane vessel); Standard; PN 6 | 1
****** ***** (deleted) |  |  | SQ 140.6 (Membrane vessel); Standard; PN 6 | 2
| 301010-50601 |  | DLV 25 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 2
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 2
- |  |  | CD 80.9 (Integrated vessel); Standard; PN 6 | 1
301021 41001 |  |  | Simply Compresso C 2.1-80 S (Compressor); PN 6 | 1
- |  |  | CD 80.9 (Integrated vessel); Standard; PN 6 | 1
301021 41003 |  |  | CD 80.9 E (Integrated vessel); Standard; PN 6 | 1
301021 41001 |  |  | Simply Compresso C 2.1-80 S (Compressor); PN 6 | 3
- |  |  | CD 80.9 (Integrated vessel); Standard; PN 6 | 3
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 3
301051-10530 |  |  | DSV 20-3.0 SOL; Diaphragm; Thread; PN 10 | 1
301051-10580 |  |  | DSV 20-8.0 SOL; Diaphragm; Thread; PN 10 | 1
301051-20530 |  |  | DSV 20-3.0 F; Diaphragm; Thread; PN 16 | 1
301051-20840 |  |  | DSV 40-4.0 F; Diaphragm; Thread; PN 16 | 1
303041-11000 |  |  | ZG 65; Standard; Flange; PN 16 | 2
303041-21100 |  |  | ZG 80 W; Standard; Welding and Groove; PN 16 | 3
303051-11000 |  |  | ZGM 65-100; Zeparo G-Force Magnet ZGM | 3
30305141000 |  |  | ZGI 65; Zeparo G-Force Insulation ZGI | 2
536 1020 |  |  | DSV 15-2.0 DGH; Diaphragm; Thread; PN 25 | 2
710 1006 |  |  | SD 80.3 (Statico); Standard | 3
*** **** (deleted) |  |  | PI (Make-up water); PN 10 | 3
813 3016 |  |  | Refill Demin 4000 (Desalination); Standard; PN 6 | 3
| 813 3121 |  | Electronic water meter; Electronic water meter with countdown function for manual make up. | 3
| 813 3120 |  | Total hardness measuring; Total hardness measuring equipment for app. 100 measurements. | 3
710 1008 |  |  | SU 140.3 (Statico); Standard | 2
| 746 2000 |  | DLV 20 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 2
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 2
710 1010 |  |  | SU 200.3 (Statico); Standard | 4
| 535 1434 |  | DLV 20; Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 8
714 2021 |  |  | DD 12.10 (Intermediate vessel); Standard; PN 10 | 3
710 1011 |  |  | SU 300.3 (Statico); Standard | 2
| 535 1434 |  | DLV 20; Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 2
714 2023 |  |  | DD 25.10 (Intermediate vessel); Standard; PN 10 | 2
*** **** (deleted) |  |  | PI (Make-up water); PN 10 | 2
710 3005 |  |  | SD 50.10 (Statico); Standard; PN 10 | 2
| 535 1434 |  | DLV 20; Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 2
*** **** (deleted) |  |  | PI (Make-up water); PN 10 | 2
*** **** (deleted) |  |  | Refill 6000 Filter (Softening); With filter; PN 6 | 2
| 813 3122 |  | Battery for WM; Internal battery for the electronic water meter equipment. | 2
711 1010 |  |  | AU 400.10 (Aquapresso vessel); Standard; PN 10 | 1
713 2003 |  |  | TU 500 E (Secondary vessel); Standard | 1
714 1006 |  |  | DU 500.6 (Intermediate vessel); Standard; PN 6 | 1
787 1340 |  |  | ZHU-ZUK/ZUKM 40; Thermal insulation (EPP) for Zeparo ZUK/ZUKM | 1
787 1440 |  |  | ZHU-ZUD/ZUM 40; Thermal insulation (EPP) for Zeparo ZHU-ZUD/ZUM | 4
787 2065 |  |  | ZHI-ZIO 50-65; Thermal insulation (Rockwool 2 part galvanized steel cladding) for Zeparo ZIO | 1
787 2100 |  |  | ZHI-ZIO 80-100; Thermal insulation (Rockwool 2 part galvanized steel cladding) for Zeparo ZIO | 1
788 2050 |  |  | ZIO 50F; Industrial; Flange; PN 10 | 1
788 2100 |  |  | ZIO 100F; Industrial; Flange; PN 10 | 1
789 1325 |  |  | ZUTX 25; Zeparo G-Force Air Vent ZUTX | 2
789 1615 |  |  | ZUTS 15; Solar; Thread; PN 10 | 2
789 1740 |  |  | ZUVS 40; Solar; Thread; PN 10 | 1
789 2140 |  |  | ZUD 40; Standard; Thread; PN 10 | 4
789 4225 |  |  | ZUKM 25; Magnetic; Thread; PN 10 | 1
810 1420 |  |  | C 10.1-3.0 Connect (Compressor) | 1
712 1000 |  |  | CU 200.6 (Primary vessel); Standard; PN 6 | 1
714 2023 |  |  | DD 25.10 (Intermediate vessel); Standard; PN 10 | 1
*** **** (deleted) |  |  | P RC (Make-up water); PN 10 | 1
813 3015 |  |  | Refill Demin 2000 (Desalination); Standard; PN 6 | 1
810 1420 |  |  | C 10.1-3.0 Connect (Compressor) | 2
712 1000 |  |  | CU 200.6 (Primary vessel); Standard; PN 6 | 2
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 2
*** **** (deleted) |  |  | V 2.1 F (Degassing); PN 6 | 2
*** **** (deleted) |  |  | P (Make-up water); PN 10 | 2
810 1420 |  |  | C 10.1-3.0 Connect (Compressor) | 3
712 1000 |  |  | CU 200.6 (Primary vessel); Standard; PN 6 | 3
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 3
810 1460 |  |  | C 10.2-3.0 Connect (Compressor) | 2
712 1000 |  |  | CU 200.6 (Primary vessel); Standard; PN 6 | 1
712 2000 |  |  | CU 200.6 E (Secondary vessel); Standard; PN 6 | 1
714 2022 |  |  | DD 18.10 (Intermediate vessel); Standard; PN 10 | 2
811 1500 |  |  | TV 4.1 E (Degassing/Pump); PN 10 | 2
710 3007 |  |  | SU 140.10 (Buffer vessel); Standard; PN 10 | 2
| 501 1038 |  | Thermometer/Manometer TH; Pressure display range 0-4 bar, temperature display range 0-120 °C, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Rear connection. | 2
811 1510 |  |  | TV 4.1 EH (Degassing/Pump); PN 10 | 2
713 1000 |  |  | TU 200 (Primary vessel); Standard | 2
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 2
| 501 1037 |  | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 2
714 2023 |  |  | DD 25.10 (Intermediate vessel); Standard; PN 10 | 2
813 3330 |  |  | P AB5 R (Make-up water); PN 10 | 2
813 3270 |  |  | Refill Demin 18000 (Desalination); Standard; PN 6 | 2
811 1510 |  |  | TV 4.1 EH (Degassing/Pump); PN 10 | 3
713 1000 |  |  | TU 200 (Primary vessel); Standard | 3
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 3
| 501 1037 |  | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 3
714 2023 |  |  | DD 25.10 (Intermediate vessel); Standard; PN 10 | 3
813 3270 |  |  | Refill Demin 18000 (Desalination); Standard; PN 6 | 3
| 813 3120 |  | Total hardness measuring; Total hardness measuring equipment for app. 100 measurements. | 3
811 1510 |  |  | TV 4.1 EH (Degassing/Pump); PN 10 | 3
713 1000 |  |  | TU 200 (Primary vessel); Standard | 3
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 3
| 500 1060 |  | DH 15; Push button valve for shut-off of manometers | 3
| 535 1434 |  | DLV 20; Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 3
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 3
813 3320 |  |  | P AB5 (Make-up water); PN 10 | 3
811 1510 |  |  | TV 4.1 EH (Degassing/Pump); PN 10 | 3
713 1000 |  |  | TU 200 (Primary vessel); Standard | 3
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 3
| 500 1060 |  | DH 15; Push button valve for shut-off of manometers | 3
| 501 1037 |  | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 3
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 3
811 1510 |  |  | TV 4.1 EH (Degassing/Pump); PN 10 | 4
713 1000 |  |  | TU 200 (Primary vessel); Standard | 4
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 4
| 500 1060 |  | DH 15; Push button valve for shut-off of manometers | 4
714 2020 |  |  | DD 8.10 (Intermediate vessel); Standard; PN 10 | 4
811 1521 |  |  | TV 6.2 EH (Degassing/Pump); PN 10 | 2
713 1000 |  |  | TU 200 (Primary vessel); Standard | 1
710 3005 |  |  | SD 50.10 (Buffer vessel); Standard; PN 10 | 2
| 535 1434 |  | DLV 20; Lockshield valve DLV, female thread on both sides, flat sealing union for direct connection to expansion vessel. | 5
713 2000 |  |  | TU 200 E (Secondary vessel); Standard | 1
714 2022 |  |  | DD 18.10 (Intermediate vessel); Standard; PN 10 | 2
812 1101 |  |  | V 4.1 E Connect (Degassing); PN 10 | 2
813 3320 |  |  | P AB5 (Make-up water); PN 10 | 2
812 1203 |  |  | V 8.1 EC Connect (Degassing); PN 10 | 1
813 3016 |  |  | Refill Demin 4000 (Desalination); Standard; PN 6 | 3
| 813 3121 |  | Electronic water meter; Electronic water meter with countdown function for manual make up. | 3
| 813 3112 |  | Key for filter; Key to change filter and cartridges. | 3
813 3330 |  |  | P AB5 R (Make-up water); PN 10 | 3
813 3270 |  |  | Refill Demin 18000 (Desalination); Standard; PN 6 | 3
| 813 3121 |  | Electronic water meter; Electronic water meter with countdown function for manual make up. | 3