## Control products (1)
Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection)
|  | Water Temperature: 6 °C | TA-FUSION-C 40 | 0.0014 m3/s |  | *****-****** | Steel DIN 2440, ISO 65 | 1
|  |  | Ametal(tm) | 10000 Pa |  | (deleted) | 50
|  |  | Thread | 9.15 turns |  |  | 0.63 m/s
|  |  | Standard |  |  |  | 102 Pa/m
PN 16; -20/120 °C
Adapter 01 |  |  | Adapter for TA-SLIDER 750, TA-MC55(Y), MC100(FSE/FSR) |  |  | *****-****** (deleted) |  | 1
|  |  | TA-MC 100/24 |  |  | 61100-001 |  | 1
Close-off Dp : 800000 Pa
Actuating time : 240; 180*; 80; 38 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
ACA71 |  |  | Position switch unit (2 switches) |  |  | 67071-100 |  | 1
ACA72 |  |  | Enclosure protection IP 65 |  |  | *****-*** (deleted) |  | 1
|  | Water Temperature: 6 °C | TBV-CM 25NF | 0.0014 m3/s |  | 52144-125 | Steel DIN 2440, ISO 65 | 1
|  |  | Ametal(tm) | 156247 Pa |  |  | 50
|  |  | Thread | pos. 10* |  |  | 0.63 m/s
|  |  | Standard |  |  |  | 102 Pa/m
PN 16; -20/120 °C
|  |  | EMO TM 24/NC (5m) |  |  | 1868-02.500 |  | 1
Close-off Dp : 975000 Pa
Actuating time : 120 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 0(2)-10 V
Output signal : -
Relay type : No relay
Fail-safe type : No
Default return position : Extending
Max. Temp. : 120°C
|  | Water Temperature: 6 °C | TA-FUSION-C 40 | 0.0014 m3/s |  | *****-****** | Steel DIN 2440, ISO 65 | 1
|  |  | Ametal(tm) | 10000 Pa |  | (deleted) | 50
|  |  | Thread | 9.15 turns |  |  | 0.63 m/s
|  |  | Standard |  |  |  | 102 Pa/m
PN 16; -20/120 °C
Adapter 01 |  |  | Adapter for TA-SLIDER 750, TA-MC55(Y), MC100(FSE/FSR) |  |  | *****-****** (deleted) |  | 1
|  |  | TA-MC 100FSE/24 |  |  | *****-*** |  | 1
|  |  | Close-off Dp : 800000 Pa |  |  | (deleted)
Actuating time : 40 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 0(2)-10 V; 0(4)-20 mA
Output signal : 0(2)-10 V; 0(4)-20 mA
Relay type : No relay
Fail-safe type : Spring return
Fail-safe position : Extending
Max. Temp. : -

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-*** (deleted) |  |  | TA-MC 100FSE/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 1
*****-*** (deleted) |  |  | ACA72; Enclosure protection IP 65 | 1
*****-****** (deleted) |  |  | TA-FUSION-C 40; Standard; Thread; PN 16; Kvs = 18.5 | 2
*****-****** (deleted) |  |  | Adapter 01; Adapter for TA-SLIDER 750, TA-MC55(Y), MC100(FSE/FSR) | 2
1868-02.500 |  |  | EMO TM 24/NC (5m); Actuating force = 125 N; Power Supply = 24 VAC; Relay type = No relay | 1
52144-125 |  |  | TBV-CM 25NF; Standard; Thread; PN 16; Kvs = 4 | 1
61100-001 |  |  | TA-MC 100/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 1
67071-100 |  |  | ACA71; Position switch unit (2 switches) | 1