## Balancing valves (1)
Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves
#1 | #2 | Water | Product | Technical Info | Radiator Info | Article N° | Pipe | Qty |  |  | §
Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection)
|  | Water Temperature: 6 °C | STAD 50 | 0.0014 m3/s |  | *****-*** | Steel DIN 2440, ISO 65 | 1
|  |  | 50 (2") | 3000 Pa |  | (deleted) | 50
|  |  | Thread | 3.7 turns |  |  | 0.63 m/s
|  |  | Without drain |  |  |  | 102 Pa/m
PN 20; -20/120 °C
Draining kit 1/2" |  |  | Can be installed during system operation. |  |  | 52179-990 |  | 1
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  | Water Temperature: 6 °C | STA 50 | 0.0014 m3/s |  | *****-*** | Steel DIN 2440, ISO 65 | 1
|  |  | 50 (2") | 3000 Pa |  | (deleted) | 50
|  |  | Thread | 3.7 turns |  |  | 0.63 m/s
|  |  | With drain 1/2" |  |  |  | 102 Pa/m
PN 20; -20/120 °C
|  | Water Temperature: 6 °C | MD 01 DN40 | 0.0014 m3/s |  | 52176-140 | Steel DIN 2440, ISO 65 | 1
|  |  | 40 (1 1/2") | Dp signal = 4165 Pa |  |  | 50
|  |  | Thread | 1908 Pa |  |  | 0.63 m/s
|  |  | PT 90 |  |  |  | 102 Pa/m
PN 20; -10/120 °C
|  | Water Temperature: 6 °C | TRIM A 20 | 0.00028 m3/s |  | 50007-120 | Steel DIN 2440, ISO 65 | 1
|  |  | 20 (3/4") | 4945 Pa |  |  | 25
|  |  | Thread | 5* turns |  |  | 0.478 m/s
|  |  | Straight |  |  |  | 145 Pa/m
PN 16; -10/120 °C
|  | Water Temperature: 6 °C | TBV 20NF | 0.00028 m3/s |  | 52138-120 | Steel DIN 2440, ISO 65 | 1
|  |  | 20 (3/4") | 8660 Pa |  |  | 25
|  |  | Thread | pos. 10* |  |  | 0.478 m/s
|  |  | Without drain |  |  |  | 145 Pa/m
PN 16; -20/120 °C

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-*** (deleted) |  |  | STA 50; With drain 1/2"; Thread; PN 20 | 1
*****-*** (deleted) |  |  | STAD 50; Without drain; Thread; PN 20 | 1
50007-120 |  |  | TRIM A 20; Straight; Thread; PN 16 | 1
52138-120 |  |  | TBV 20NF; Without drain; Thread; PN 16 | 1
52176-140 |  |  | MD 01 DN40; PT 90; Thread; PN 20 | 1
52179-006 |  |  | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 2
52179-016 |  |  | Extension for measuring point M14x1; Length 71 mm. Suitable when insulation is used. | 2
52179-990 |  |  | Draining kit 1/2"; Can be installed during system operation. | 1