## Control products (1)
Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection)
|  | Water Temperature: 6 °C | CV 216 RGA DN32 | 0.0014 m3/s |  | 60233-132 | Steel DIN 2440, ISO 65 | 1
|  |  | Kvs = 12.5 | 16000 Pa |  |  | 50
|  |  | Bronze | - |  |  | 0.63 m/s
|  |  | Thread |  |  |  | 102 Pa/m
Standard
PN 16; -15/150 °C
ACV 11 |  |  | Internal thread connect. parts of bronze |  |  | 68011-032 |  | 1
ACV 12 |  |  | Plug made of CrNi steel 1.4305 |  |  | 68012-032 |  | 1
ACV 13 |  |  | Stem heater |  |  | 68013-015 |  | 1
ACV 15 |  |  | Sealing FKM |  |  | 68015-032 |  | 1
ACV 16 |  |  | Technical silicon free version |  |  | 68016-032 |  | 1
|  |  | TA-MC 100/115 |  |  | 61100-302 |  | 1
Close-off Dp : 900000 Pa
Actuating time : 168; 126*; 56; 26.6 s
IP auto(man.) : 54
Power Supply : 115 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
ACA71 |  |  | Position switch unit (2 switches) |  |  | 67071-100 |  | 1
ACA72 |  |  | Enclosure protection IP 65 |  |  | *****-*** (deleted) |  | 1
|  | Water Temperature: 6 °C | CV 216 MZ DN25 | 0.0014 m3/s |  | *****-*** | Steel DIN 2440, ISO 65 | 1
|  |  | Kvs = 6.3 | 62987 Pa |  | (deleted) | 50
|  |  | Brass | - |  |  | 0.63 m/s
|  |  | Thread |  |  |  | 102 Pa/m
Standard
PN 16; 0/120 °C
ACV 1 - 216/316 MZ 25 |  |  | Internal thread connect. parts |  |  | 68001-025 |  | 1
|  |  | TA-MC 15/24 |  |  | *****-*** |  | 1
|  |  | Close-off Dp : 150000 Pa |  |  | (deleted)
Actuating time : 130 s
IP auto(man.) : 40
Power Supply : 24 VAC; 24 VDC
Input : 3-point; 0(2)-10 V
Output signal : -
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
|  | Water Temperature: 6 °C | CV 206 GG DN32 | 0.0014 m3/s |  | 60215-132 | Steel DIN 2440, ISO 65 | 1
|  |  | Kvs = 12.5 | 16000 Pa |  |  | 50
|  |  | Cast iron | - |  |  | 0.63 m/s
|  |  | Flange |  |  |  | 102 Pa/m
Standard
PN 6; -10/150 °C
ACV 12 |  |  | Plug made of CrNi steel 1.4305 |  |  | 68012-032 |  | 1
ACV 13 |  |  | Stem heater |  |  | 68013-015 |  | 1
ACV 14 |  |  | Epoxy resin special varnish |  |  | 68014-032 |  | 1
ACV 15 |  |  | Sealing FKM |  |  | 68015-032 |  | 1
ACV 16 |  |  | Technical silicon free version |  |  | 68016-032 |  | 1
|  |  | TA-MC 100/24 |  |  | 61100-001 |  | 1
Close-off Dp : 600000 Pa
Actuating time : 168; 126*; 56; 26.6 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
|  | Water Temperature: 6 °C | CV 206 GG DN32 | 0.0014 m3/s |  | 60215-132 | Steel DIN 2440, ISO 65 | 1
|  |  | Kvs = 12.5 | 16000 Pa |  |  | 50
|  |  | Cast iron | - |  |  | 0.63 m/s
|  |  | Flange |  |  |  | 102 Pa/m
Standard
PN 6; -10/150 °C
ACV 12 |  |  | Plug made of CrNi steel 1.4305 |  |  | 68012-032 |  | 1
ACV 13 |  |  | Stem heater |  |  | 68013-015 |  | 1
ACV 14 |  |  | Epoxy resin special varnish |  |  | 68014-032 |  | 1
ACV 15 |  |  | Sealing FKM |  |  | 68015-032 |  | 1
ACV 16 |  |  | Technical silicon free version |  |  | 68016-032 |  | 1
|  |  | TA-MC 100/24 |  |  | 61100-001 |  | 1
Close-off Dp : 600000 Pa
Actuating time : 168; 126*; 56; 26.6 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
ACA71 |  |  | Position switch unit (2 switches) |  |  | 67071-100 |  | 1
ACA72 |  |  | Enclosure protection IP 65 |  |  | *****-*** (deleted) |  | 1
|  | Water Temperature: 6 °C | CV 216 GG DN25 | 0.0014 m3/s |  | 60235-225 | Steel DIN 2440, ISO 65 | 1
|  |  | Kvs = 10 | 25000 Pa |  |  | 50
|  |  | Cast iron | - |  |  | 0.63 m/s
|  |  | Flange |  |  |  | 102 Pa/m
Standard
PN 16; -10/150 °C
ACV 14 |  |  | Epoxy resin special varnish |  |  | 68014-025 |  | 1
ACV 16 |  |  | Technical silicon free version |  |  | 68016-025 |  | 1
|  |  | TA-MC 55Y |  |  | 61055-003 |  | 1
Close-off Dp : 750000 Pa
Actuating time : 126; 70* s
IP auto(man.) : 54(30)
Power Supply : 24 VAC
Input : 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-*** (deleted) |  |  | TA-MC 15/24; Actuating force = 150 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
*****-*** (deleted) |  |  | CV 216 MZ DN25; Standard; Thread; PN 16; Kvs = 6.3 | 1
*****-*** (deleted) |  |  | ACA72; Enclosure protection IP 65 | 2
60215-132 |  |  | CV 206 GG DN32; Standard; Flange; PN 6; Kvs = 12.5 | 2
60233-132 |  |  | CV 216 RGA DN32; Standard; Thread; PN 16; Kvs = 12.5 | 1
60235-225 |  |  | CV 216 GG DN25; Standard; Flange; PN 16; Kvs = 10 | 1
61055-003 |  |  | TA-MC 55Y; Actuating force = 600 N; Power Supply = 24 VAC; Relay type = No relay | 1
61100-001 |  |  | TA-MC 100/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 2
61100-302 |  |  | TA-MC 100/115; Actuating force = 1000 N; Power Supply = 115 VAC; Relay type = No relay | 1
67071-100 |  |  | ACA71; Position switch unit (2 switches) | 2
68001-025 |  |  | ACV 1 - 216/316 MZ 25; Internal thread connect. parts | 1
68011-032 |  |  | ACV 11; Internal thread connect. parts of bronze | 1
68012-032 |  |  | ACV 12; Plug made of CrNi steel 1.4305 | 3
68013-015 |  |  | ACV 13; Stem heater | 3
68014-025 |  |  | ACV 14; Epoxy resin special varnish | 1
68014-032 |  |  | ACV 14; Epoxy resin special varnish | 2
68015-032 |  |  | ACV 15; Sealing FKM | 3
68016-025 |  |  | ACV 16; Technical silicon free version | 1
68016-032 |  |  | ACV 16; Technical silicon free version | 3