## Dp controllers (1)
Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets
#1 | #2 | Water | Product | Technical Info | Radiator Info | Article N° | Pipe | Qty |  |  | §
Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection)
|  | Water Temperature: 6 °C | DA 516 DN25/32 | 0.0014 m3/s |  | 52795-025 | Steel DIN 2440, ISO 65 | 1
|  |  | 25 (1") | Dpl unknown |  |  | 50
|  |  | Thread -> 25 (1") | Dpmin = 17361 Pa |  |  | 0.63 m/s
|  |  | PT 90 | Scheme A |  |  | 102 Pa/m
[5000-30000] Pa
PN 25; -10/120 °C
|  | Water Temperature: 6 °C | STAP 40 | 0.0014 m3/s |  | 52265-140 | Steel DIN 2440, ISO 65 | 1
|  |  | 40 (1 1/2") | Dpl unknown |  |  | 50
|  |  | Thread | Dpmin = 15259 Pa |  |  | 0.63 m/s
|  |  | Standard | Scheme B |  |  | 102 Pa/m
[10000-40000] Pa
PN 16; -20/120 °C
|  |  | STAD 50 | 0.0014 m3/s |  | *****-*** |  | 1
|  |  | 50 (2") | 3000 Pa |  | (deleted)
|  |  | Thread | 3.7 turns
With drain 1/2"
PN 20; -20/120 °C
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  | Water Temperature: 6 °C | DA 516 DN25/32 | 0.0014 m3/s |  | 52795-125 | Steel DIN 2440, ISO 65 | 1
|  |  | 25 (1") | Dpl unknown |  |  | 50
|  |  | Thread -> 25 (1") | Dpmin = 17361 Pa |  |  | 0.63 m/s
|  |  | PT 90 | Scheme C |  |  | 102 Pa/m
[10000-60000] Pa
PN 25; -10/120 °C
Impulse pipe connection kit (1/2") |  |  | For connecting 6 mm copper impulse pipe to STAD with 1/2" drain. |  |  | 52762-006 |  | 1
Measuring point, two-way with 6mm copper pipe side connection. |  |  | For connection of 6mm impulse pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. |  |  | 52179-206 |  | 1
|  |  | STAD 50 | 0.0014 m3/s |  | *****-*** |  | 1
|  |  | 50 (2") | 3000 Pa |  | (deleted)
|  |  | Thread | 3.7 turns
With drain 3/4"
PN 20; -20/120 °C
Scheme A
(DA 516)
Scheme B
(STAP)
Scheme C
(DA 516)

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-*** (deleted) |  |  | STAD 50; With drain 3/4"; Thread; PN 20 | 1
*****-*** (deleted) |  |  | STAD 50; With drain 1/2"; Thread; PN 20 | 1
52179-006 |  |  | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 2
52179-016 |  |  | Extension for measuring point M14x1; Length 71 mm. Suitable when insulation is used. | 2
52179-206 |  |  | Measuring point, two-way with 6mm copper pipe side connection.; For connection of 6mm impulse pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. | 1
52265-140 |  |  | STAP 40; [10000-40000] Pa; Standard; Thread; PN 16 | 1
52759-025 |  |  | Conn. Piece: Thread, 25 (1") | 4
52762-006 |  |  | Impulse pipe connection kit (1/2"); For connecting 6 mm copper impulse pipe to STAD with 1/2" drain. | 1
52795-025 |  |  | DA 516 DN25/32; [5000-30000] Pa; PT 90; Thread; PN 25 | 1
52795-125 |  |  | DA 516 DN25/32; [10000-60000] Pa; PT 90; Thread; PN 25 | 1