## Control products (1)
Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection) | Pressure independent control valves / Actuators (from individual selection)
|  | Water Temperature: 6 °C | TA-Fusion-P 32 | 0.00028 m3/s |  | *****-****** | Steel DIN 2440, ISO 65 | 1
|  |  | Ametal(tm) | Dpmin = 13016 Pa |  | (deleted) | 25
|  |  | Thread | 1.82 turns |  |  | 0.478 m/s
|  |  | Standard |  |  |  | 145 Pa/m
PN 16; -20/120 °C
Adapter 01 |  |  | Adapter for TA-SLIDER 750, TA-MC55(Y), MC100(FSE/FSR) |  |  | *****-****** (deleted) |  | 1
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  |  | TA-MC 55Y |  |  | 61055-003 |  | 1
Close-off Dp : 800000 Pa
Actuating time : 180; 100* s
IP auto(man.) : 54(30)
Power Supply : 24 VAC
Input : 0(2)-10 V; 0(4)-20 mA
Output signal : 0-10 V
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : -
|  | Water Temperature: 6 °C | TA-Modulator 25 | 4.167e-5 m3/s |  | 52164-325 | Steel DIN 2440, ISO 65 | 1
|  |  | Ametal(tm) | Dpmin = 16000 Pa |  |  | 15
|  |  | Thread male | pos. 0.5 |  |  | 0.207 m/s
|  |  | Standard |  |  |  | 38.2 Pa/m
PN 16; -10/90 °C
|  |  | TA-Slider 160 (1m) |  |  | 322224-10111 |  | 1
Close-off Dp : 400000 Pa
Actuating time : 65.1 s
IP auto(man.) : 54
Power Supply : 24 VAC; 24 VDC
Input : 0(2)-10 V
Output signal : -
Relay type : No relay
Fail-safe type : No
Default return position : None
Max. Temp. : 120°C

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
*****-****** (deleted) |  |  | TA-Fusion-P 32; Standard; Thread; PN 16 | 1
*****-****** (deleted) |  |  | Adapter 01; Adapter for TA-SLIDER 750, TA-MC55(Y), MC100(FSE/FSR) | 1
322224-10111 |  |  | TA-Slider 160 (1m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
52164-325 |  |  | TA-Modulator 25; Standard; Thread male; PN 16 | 1
52179-006 |  |  | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 2
61055-003 |  |  | TA-MC 55Y; Actuating force = 600 N; Power Supply = 24 VAC; Relay type = No relay | 1