## Pressure maintenance prod. (1)
Selected pressure maintenance products
Calculated pressure maintenance selection
Input data |  |  |  |  | Calculated data
Description |  |  |  | Value | Description |  | Value
Application type |  |  |  | Cooling | System expansion coefficient [e] |  | 0.00990
Fluid type: | Water |  |  |  | System expansion volume [Ve] |  | 4.95e-5 m3
Norm |  |  |  |  | Total expansion volume [Ve,tot] |  | 4.95e-5 m3
System volume [Vs] |  |  |  | 0.005 m3 | Min. water reserve [Vwr,min] |  | 0.003 m3
Installed power [Qs] |  |  |  | 50000 W | Vessel net volume [Vn] |  | 0.0031 m3
Static height [Hst] |  |  |  | 0 m | Water reserve [Vwr] |  | 0.005 m3
Min. required equipment pressure [pz] |  |  |  | - | Contracted volume [Vcontr] |  | 4.483e-6 m3
Safety valve response pressure [pSV] |  |  |  | 300000 Pa | Vapour over-pressure [pv] |  | 0 Pa
Maximum temperature [tsmax] |  |  |  | 45 °C | Minimum pressure [p0] |  | 30000 Pa
Supply temperature |  |  |  | 6 °C | Initial pressure [pa] |  | 244777 Pa
Return temperature |  |  |  | 12 °C | Filling pressure [pfill] |  | 244777 Pa
Minimum temperature [tsmin] |  |  |  | 6 °C | Final pressure [pe] |  | 250000 Pa
Fill temperature |  |  |  | 15 °C | Specific flowrate of equalization volume [qN/Q] |  | -
Pressurisation on |  |  |  | pump suction | Necessary flowrate of equalization volume [qN] |  | -
Pump head |  |  |  | - | Pressure factor [PF] |  | 1.59
Max width |  |  |  | 0 m | Required nominal volume |  | 0.0049 m3
Max height |  |  |  | 0 m | Expansion pipe up to (10 m) [DNe] |  | 20 (3/4")
[5 empty] | Expansion pipe up to (30 m) [DNe] |  | 20 (3/4")
Product
#1 |  | #2 | Product |  |  | Article N° |  | Qty | §
|  |  | Statico |  |  | 710 1000 |  | 1
SD 8.3
Connection = Thread ISO228 Male R
Nom. volume = 0.008 m3
PS = 300000 Pa
Temp. range = 5/70 °C
Weight = 3.5 kg
Max. weight = 11.5 kg
DH 15; PN 25; -20/100 °C | [5 empty] | Push button valve for shut-off of manometers |  |  |  | 1
DLV 15; PN 16 | [5 empty] | Lockshield valve DLV, female thread on both sides, screw connection on the vessel connection side. |  |  |  | 1
Manometer H; -10/60 °C | [5 empty] | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. |  |  |  | 1
Calculated pressure maintenance selection
Input data |  |  |  |  | Calculated data
Description |  |  |  | Value | Description |  | Value
Application type |  |  |  | Cooling | System expansion coefficient [e] |  | 0.00990
Fluid type: | Water |  |  |  | System expansion volume [Ve] |  | 4.95e-5 m3
Norm |  |  |  |  | Total expansion volume [Ve,tot] |  | 4.95e-5 m3
System volume [Vs] |  |  |  | 0.005 m3 | Min. water reserve [Vwr,min] |  | 0.003 m3
Installed power [Qs] |  |  |  | 50000 W | Vessel net volume [Vn] |  | 0.0031 m3
Static height [Hst] |  |  |  | 0 m | Vapour over-pressure [pv] |  | 0 Pa
Min. required equipment pressure [pz] |  |  |  | - | Minimum pressure [p0] |  | 30000 Pa
Safety valve response pressure [pSV] |  |  |  | 300000 Pa | Initial pressure [pa] |  | 60000 Pa
Maximum temperature [tsmax] |  |  |  | 45 °C | Target pressure [pman] |  | 70000 Pa
Supply temperature |  |  |  | 6 °C | Final pressure [pe] |  | 80000 Pa
Return temperature |  |  |  | 12 °C | Specific flowrate of equalization volume [qN/Q] |  | 1.0667e-10 m3/s/W
Minimum temperature [tsmin] |  |  |  | 6 °C | Necessary flowrate of equalization volume [qN] |  | 5.333e-6 m3/s
Pressurisation on |  |  |  | pump suction | Pressure factor [PF] |  | 1.10
Pump head |  |  |  | - | Required nominal volume |  | 0.0034 m3
Max width |  |  |  | 0 m | Expansion pipe up to (10 m) [DNe] |  | 20 (3/4")
Max height |  |  |  | 0 m | Expansion pipe up to (30 m) [DNe] |  | 20 (3/4")
Product
#1 |  | #2 | Product |  |  | Article N° |  | Qty | §
|  |  | TecBox - Compresso (Compressor) |  |  | 810 1411 |  | 1
C 10.1-3.75 F Connect
PS = 375000 Pa
Power = 600 W
Supply voltage = 230 VAC
|  |  | Primary vessel |  |  | 712 1000 |  | 1
CU 200.6
Connection = Thread ISO228 Female RP
Nom. volume = 0.2 m3
PS = 600000 Pa
Temp. range = 5/70 °C
Weight = 34 kg
Max. weight = 234 kg
Calculated pressure maintenance selection
Input data |  |  |  |  | Calculated data
Description |  |  |  | Value | Description |  | Value
Application type |  |  |  | Cooling | System expansion coefficient [e] |  | 0.00990
Fluid type: | Water |  |  |  | System expansion volume [Ve] |  | 4.95e-5 m3
Norm |  |  |  |  | Total expansion volume [Ve,tot] |  | 4.95e-5 m3
System volume [Vs] |  |  |  | 0.005 m3 | Min. water reserve [Vwr,min] |  | 0.003 m3
Installed power [Qs] |  |  |  | 50000 W | Vessel net volume [Vn] |  | 0.0031 m3
Static height [Hst] |  |  |  | 0 m | Vapour over-pressure [pv] |  | 0 Pa
Min. required equipment pressure [pz] |  |  |  | - | Minimum pressure [p0] |  | 30000 Pa
Safety valve response pressure [pSV] |  |  |  | 300000 Pa | Initial pressure [pa] |  | 60000 Pa
Maximum temperature [tsmax] |  |  |  | 45 °C | Target pressure [pman] |  | 70000 Pa
Supply temperature |  |  |  | 6 °C | Final pressure [pe] |  | 80000 Pa
Return temperature |  |  |  | 12 °C | Specific flowrate of equalization volume [qN/Q] |  | 1.0667e-10 m3/s/W
Minimum temperature [tsmin] |  |  |  | 6 °C | Necessary flowrate of equalization volume [qN] |  | 5.333e-6 m3/s
Pressurisation on |  |  |  | pump suction | Pressure factor [PF] |  | 1.10
Pump head |  |  |  | - | Required nominal volume |  | 0.0034 m3
Max width |  |  |  | 0 m | Expansion pipe up to (10 m) [DNe] |  | 20 (3/4")
Max height |  |  |  | 0 m | Expansion pipe up to (30 m) [DNe] |  | 20 (3/4")
Product
#1 |  | #2 | Product |  |  | Article N° |  | Qty | §
|  |  | TecBox - Compresso (Compressor) |  |  | 810 1411 |  | 1
C 10.1-3.75 F Connect
PS = 375000 Pa
Power = 600 W
Supply voltage = 230 VAC
|  |  | Primary vessel |  |  | 712 1005 |  | 1
CU 800.6
Connection = Thread ISO228 Female RP
Nom. volume = 0.8 m3
PS = 600000 Pa
Temp. range = 5/70 °C
Weight = 98 kg
Max. weight = 898 kg

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
710 1000 |  |  | SD 8.3 (Statico); Standard | 1
| 500 1060 |  | DH 15; Push button valve for shut-off of manometers | 1
| 535 1432 |  | DLV 15; Lockshield valve DLV, female thread on both sides, screw connection on the vessel connection side. | 1
| 501 1037 |  | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 1
810 1411 |  |  | C 10.1-3.75 F Connect (Compressor) | 1
712 1005 |  |  | CU 800.6 (Primary vessel); Standard; PN 6 | 1
810 1411 |  |  | C 10.1-3.75 F Connect (Compressor) | 1
712 1000 |  |  | CU 200.6 (Primary vessel); Standard; PN 6 | 1