## Change-over (1)
Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations | Selected change-over stations
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection) | Change-over stations (from individual selection)
6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve
|  | Water Cooling temp.: 6 / 12 °C Heating temp.: 70 / 50 °C | TA-6-way valve DN20 | Cooling info: |  | 322031-30504 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 4 | 0.00025 m3/s |  |  | 25 (1")
|  |  | Dezincification resistant brass | 5062 Pa |  |  | 0.43 m/s
|  |  | Thread | Heating info: |  |  | 120 Pa/m
|  |  | Non-plated (raw finish) | 8.333e-5 m3/s
|  |  | PN 16; -10/120 °C | 550 Pa
|  |  | TA-M106 CO |  |  | 322042-90000 |  | 1
Actuating time : 1.44 s/deg.
IP auto(man.) : 43
Power Supply : 24 VAC
Input : 3-point
Output signal : -
Relay type : No relay
Max. Temp. : 80.0°C
Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve
|  |  | TA-Modulator 20 | Dp min. cooling = 14736 Pa |  | 52164-320 |  | 1
|  |  | Kvs = 2.66 | Dp min. heating = 13762 Pa
Ametal(tm)
Thread male
Standard
PN 16; -10/90 °C
6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve
|  | Water Cooling temp.: 6 / 12 °C Heating temp.: 70 / 50 °C | TA-6-way valve DN15-20 | Cooling info: |  | 322031-30501 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 2.8 | 0.00025 m3/s |  |  | 25 (1")
|  |  | Dezincification resistant brass | 10332 Pa |  |  | 0.43 m/s
|  |  | M.T. Eurocone | Heating info: |  |  | 120 Pa/m
|  |  | Non-plated (raw finish) | 8.333e-5 m3/s
|  |  | PN 16; -10/120 °C | 1122 Pa
|  |  | TA-M106 CO |  |  | 322042-90000 |  | 1
Actuating time : 1.44 s/deg.
IP auto(man.) : 43
Power Supply : 24 VAC
Input : 3-point
Output signal : -
Relay type : No relay
Max. Temp. : 80.0°C
Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve | Pressure indep. balancing & control valve
|  |  | TA-Compact-P 25 | Dp min. cooling = 16562 Pa |  | 52164-025 |  | 1
|  |  | Kvs = 5.6 | Dp min. heating = 15700 Pa
Ametal(tm)
Thread male
Standard
PN 16; -10/90 °C
|  |  | TA-Slider 160 CO (5m HF) |  |  | 322224-10516 |  | 1
Close-off Dp : 400000 Pa
Actuating time : 40 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 0(2)-10 V
Output signal : 0(2)-10 V
Relay type : Relay change-over
Fail-safe type : No
Default return position : None
Max. Temp. : 120°C
6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve
|  |  | TA-6-way valve DN15 | Cooling info: |  | 322031-30403 |  | 1
|  |  | Kvs = 1.25 | 0.00025 m3/s
|  |  | Dezincification resistant brass | 51839 Pa
|  |  | M.T. Eurocone | Heating info:
|  |  | Non-plated (raw finish) | 8.333e-5 m3/s
|  |  | PN 16; -10/120 °C | 5632 Pa
|  |  | TA-M106 230 VAC |  |  | 322204-29001 |  | 1
Actuating time : 1.44 s/deg.
IP auto(man.) : 43
Power Supply : 230 VAC
Input : 3-point
Output signal : -
Relay type : No relay
Max. Temp. : 80.0°C
Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side) | Pressure indep. balancing & control valve (Cooling side)
|  | Water Cooling temp.: 6 / 12 °C | TA-Compact-P 20 | 0.00025 m3/s |  | 52164-020 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 3.03 | Dpmin = 14769 Pa |  |  | 25 (1")
|  |  | Ametal(tm) | Preset.: pos. 7 |  |  | 0.43 m/s
|  |  | Thread male |  |  |  | 120 Pa/m
Standard
PN 16; -10/90 °C
Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side) | Pressure indep. balancing & control valve (Heating side)
|  | Water Heating temp.: 70 / 50 °C | TA-Compact-P 15 | 8.333e-5 m3/s |  | 52164-015 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 1.28 | Dpmin = 14119 Pa |  |  | 15 (1/2")
|  |  | Ametal(tm) | Preset.: pos. 5 |  |  | 0.414 m/s
|  |  | Thread male |  |  |  | 224 Pa/m
Standard
PN 16; -10/90 °C
6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve | 6-way valve
with STAD |  |  | TA-6-way valve DN15-20 | Cooling info: |  | 322031-30500 |  | 1
|  |  | Kvs = 2.8 | 0.00025 m3/s
|  |  | Dezincification resistant brass | 10332 Pa
|  |  | M.T. Flat faced ends | Heating info:
|  |  | Non-plated (raw finish) | 8.333e-5 m3/s
|  |  | PN 16; -10/120 °C | 1122 Pa
|  |  | TA-M106 230 VAC |  |  | 322204-29001 |  | 1
Actuating time : 1.44 s/deg.
IP auto(man.) : 43
Power Supply : 230 VAC
Input : 3-point
Output signal : -
Relay type : No relay
Max. Temp. : 80.0°C
Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side) | Balancing valve (Cooling side)
|  | Water Cooling temp.: 6 / 12 °C | STAD* 20 | 0.00025 m3/s |  | 52851-620 | ** Generic Steel Pipes ** | 1
|  |  | 20 (3/4") | 3000 Pa |  |  | 25 (1")
|  |  | Thread | 3.9 turns |  |  | 0.43 m/s
|  |  | With drain 3/4" |  |  |  | 120 Pa/m
PN 25; -20/120 °C
Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side) | Balancing valve (Heating side)
|  | Water Heating temp.: 70 / 50 °C | STAD* 10 | 8.333e-5 m3/s |  | 52851-010 | ** Generic Steel Pipes ** | 1
|  |  | 10 (3/8") | 4749 Pa |  |  | 15 (1/2")
|  |  | Thread | 4* turns |  |  | 0.414 m/s
|  |  | Without drain |  |  |  | 224 Pa/m
PN 25; -20/120 °C

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
Article N° |  |  | Description | Qty
322031-30403 |  |  | TA-6-way valve DN15; Non-plated (raw finish); M.T. Eurocone; PN 16; Kvs = 1.25 | 1
322031-30500 |  |  | TA-6-way valve DN15-20; Non-plated (raw finish); M.T. Flat faced ends; PN 16; Kvs = 2.8 | 1
322031-30501 |  |  | TA-6-way valve DN15-20; Non-plated (raw finish); M.T. Eurocone; PN 16; Kvs = 2.8 | 1
322031-30504 |  |  | TA-6-way valve DN20; Non-plated (raw finish); Thread; PN 16; Kvs = 4 | 1
322042-90000 |  |  | TA-M106 CO; Actuating torque = 8 N; Power Supply = 24 VAC; Relay type = No relay | 2
322204-29001 |  |  | TA-M106 230 VAC; Actuating torque = 8 N; Power Supply = 230 VAC; Relay type = No relay | 2
322224-10516 |  |  | TA-Slider 160 CO (5m HF); Actuating force = 160 N; Power Supply = 24 VAC; Relay type = Relay change-over | 1
52164-015 |  |  | TA-Compact-P 15; Standard; Thread male; PN 16 | 1
52164-020 |  |  | TA-Compact-P 20; Standard; Thread male; PN 16 | 1
52164-025 |  |  | TA-Compact-P 25; Standard; Thread male; PN 16 | 1
52164-320 |  |  | TA-Modulator 20; Standard; Thread male; PN 16 | 1
52851-010 |  |  | STAD* 10; Without drain; Thread; PN 25 | 1
52851-620 |  |  | STAD* 20; With drain 3/4"; Thread; PN 25 | 1