## Valves export (1)
Technical informations | #1 |  | #2 | Primary product | [17 empty] | Secondary product | [21 empty] | Selection mode
|  |  |  | Product | [6 empty] | Technical informations | [7 empty] | Article N° | Victaulic Nr. | Qty | Product | [14 empty] | Technical informations |  |  |  | Article N° | Victaulic Nr. | Qty
|  |  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Flow | Power/DT | Dp | Dpl | Dpmin | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [9 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
| Chiller min. flow Bypass |  |  | TA-Fusion-P 5" | Ductile iron |  | ANSI Flange | US specific |  | Press. rate250 psi-350 psi; -20/120 °C | 0,031 m3/s |  | Dpmin = 28712 Pa |  |  | 9,79 turns |  |  | 22202-001125 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | [9 empty] | 32222610110 |  | 1 | Individual selection
|  | Cv accessory |  | Adapter 03 ; Adapter for TA-SLIDER 750/1250, TA-MC55(Y), TA-MC100(FSE/FSR) actuators | [14 empty] | 22413-001055 |  | 1
| OAHU-LB-2-1-CC-1 |  |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,012 m3/s |  | Dp=5602 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| OAHU-LB-2-1-CC-2 |  |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,012 m3/s |  | Dp=5602 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| OAHU-LB-2-1-CC-3 |  |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,012 m3/s |  | Dp=5602 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| OAHU-LB-2-1-CC-4 |  |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,012 m3/s |  | Dp=5602 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| AHU-O-4-1-CC-1 |  |  | STAF-SG 3" |  | 3" (80) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,0057 m3/s |  | Dp=3000 Pa |  |  | 7,94 turns |  |  | 52182-980 |  | 1 | [22 empty] | Individual selection
| AHU-O-4-1-CC-2 |  |  | STAF-SG 3" |  | 3" (80) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,0057 m3/s |  | Dp=3000 Pa |  |  | 7,94 turns |  |  | 52182-980 |  | 1 | [22 empty] | Individual selection
| CH-1 |  |  | STAF-SG 8" |  | 8" (200) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,047 m3/s |  | Dp=4827 Pa |  |  | 12,00* turns |  |  | 52182-993 |  | 1 | [22 empty] | Individual selection
| CH-2 |  |  | STAF-SG 8" |  | 8" (200) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,047 m3/s |  | Dp=4827 Pa |  |  | 12,00* turns |  |  | 52182-993 |  | 1 | [22 empty] | Individual selection
| CH-3 |  |  | STAF-SG 8" |  | 8" (200) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,047 m3/s |  | Dp=4827 Pa |  |  | 12,00* turns |  |  | 52182-993 |  | 1 | [22 empty] | Individual selection
| *A.1.1.1 |  | FCU-PH-2-2 | TA-Modulator 1 1/2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0011 m3/s |  | Dpmin = 23718 Pa |  |  | 1,60 turns |  |  | 52164-340 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222510111 |  | 1 | Hydraulic Network
| *A.1.1.2 |  | FCU-PH-2-1 | TA-Modulator 1 1/2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0011 m3/s |  | Dpmin = 23718 Pa |  |  | 1,60 turns |  |  | 52164-340 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222510111 |  | 1 | Hydraulic Network
| *A.1.1.3 |  | OAHU-LB-2-1 | TA-Fusion-P 6"NF | Ductile iron |  | ANSI Flange | US specific |  | Press. rate250 psi-350 psi; -20/120 °C | 0,05 m3/s |  | Dpmin = 37086 Pa |  |  | 9,65 turns |  |  | 22202-001150 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.2 |  | C-L01-DPCV-01 | STAP 3" |  | 3" (80) | ANSI Flange | Standard | [40000-160000] Pa | Press. rate300 psi; -10/120 °C | 0,0043 m3/s |  |  | Dpl = 69538 Pa | 8048 Pa | 28,06 turns | Hmin = 80956 Pa |  |  | V030794223 | 1 | STAF-SG 2 1/2" | [10 empty] | 2 1/2" (65) | ANSI Flange | Standard | Press. rate300 psi; -20/120 °C | 0,0043 m3/s |  | Dp=3370 Pa | 8,00* turns | 52182-965 |  | 1 | Hydraulic Network
| *A.1.2.1.1 |  | FCU-LB-1-7 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00033 m3/s |  | Dp = 47671 Pa |  |  | pos. 4,0 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.1.2 |  | FCU-LB-1-8 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00066 m3/s |  | Dp = 47480 Pa |  |  | pos. 8,4 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.1.3 |  | FCU-LB-1-9 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00043 m3/s |  | Dp = 47992 Pa |  |  | pos. 5,3 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.2 |  | CRAC-LB-1-2 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00033 m3/s |  | Dp = 33734 Pa |  |  | pos. 4,8 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.3 |  | FCU-LB-1-6 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00052 m3/s |  | Dp = 41620 Pa |  |  | pos. 7,4 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.4 |  | FCU-LB-1-5 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00054 m3/s |  | Dp = 37383 Pa |  |  | pos. 7,9 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.5 |  | FCU-LB-1-4 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00043 m3/s |  | Dp = 35466 Pa |  |  | pos. 6,4 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.6 |  | FCU-LB-1-3 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00034 m3/s |  | Dp = 27466 Pa |  |  | pos. 5,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.7 |  | FCU-LB-1-2 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00056 m3/s |  | Dp = 24967 Pa |  |  | pos. 10,0* |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.8 |  | FCU-LB-1-1 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00019 m3/s |  | Dp = 25641 Pa |  |  | pos. 7,5 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3 |  | C-L01-DPCV-02 | STAP 2" |  | 2" (50) | NPT thread | Standard | [20000-80000] Pa | Press. rate250 psi; -20/120 °C | 0,0015 m3/s |  |  | Dpl = 61315 Pa | 5000 Pa | 34,82 turns | Hmin = 69315 Pa |  |  | V020793CBV | 1 | STAD* 2" | [10 empty] | 2" (50) | NPT thread | Without drain | Press. rate350 psi; -20/120 °C | 0,0015 m3/s |  | Dp=3000 Pa | 3,81 turns | 52851-550 |  | 1 | Hydraulic Network
| *A.1.3.1 |  | CRAC-LB-1-1 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00061 m3/s |  | Dp = 31338 Pa |  |  | pos. 9,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.2 |  | FCU-LB-1-10 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00018 m3/s |  | Dp = 46414 Pa |  |  | pos. 5,0 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.3 |  | FCU-LB-1-11 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00067 m3/s |  | Dp = 36225 Pa |  |  | pos. 10,0* |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4.1 |  | FCU-CP-1-1 | TA-Modulator 1 1/2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0015 m3/s |  | Dpmin = 23828 Pa |  |  | 1,85 turns |  |  | 52164-340 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222510111 |  | 1 | Hydraulic Network
| *A.1.4.2 |  | KMAU-C-2-1 | TA-Modulator 2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0025 m3/s |  | Dpmin = 24489 Pa |  |  | 1,74 turns |  |  | 52164-350 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222510111 |  | 1 | Hydraulic Network
| *A.1.4.3 |  | CRAC-C-1-1 | TA-Modulator 1" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,00033 m3/s |  | Dpmin = 17914 Pa |  |  | pos. 5,9 |  |  | 52164-325 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 400000 Pa | Actuating time : 65,1 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4.4 |  | AHU-C-1-1 | TA-Modulator 3" | Ametal(tm) |  | Flange | US specific |  | Press. rate350 psi; -20/120 °C | 0,0095 m3/s |  | Dpmin = 29383 Pa |  |  | 4,79 turns |  |  | 322021-11103 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.5 |  | CRAC-O-1-2 | TA-Modulator 3/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,00015 m3/s |  | Dpmin = 13973 Pa |  |  | pos. 4,6 |  |  | 52164-320 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 400000 Pa | Actuating time : 40,4 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.6 |  | AHU-CL-1-1 | TA-Modulator 2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0018 m3/s |  | Dpmin = 22541 Pa |  |  | 1,45 turns |  |  | 52164-350 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222510111 |  | 1 | Hydraulic Network
| *A.1.7.1.1 |  | AHU-O-2-1 | TA-Modulator 3" | Ametal(tm) |  | Flange | US specific |  | Press. rate350 psi; -20/120 °C | 0,0098 m3/s |  | Dpmin = 29627 Pa |  |  | 4,87 turns |  |  | 322021-11103 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.7.1.2 |  | CARC-O-2-1 | TA-Modulator 1 1/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -20/120 °C | 0,00061 m3/s |  | Dpmin = 19677 Pa |  |  | pos. 5,1 |  |  | 52164-332 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 600000 Pa | Actuating time : 65,6 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.7.2.1 |  | AHU-O-3-1 | TA-Fusion-P 4" | Ductile iron |  | ANSI Flange | US specific |  | Press. rate250 psi-350 psi; -20/120 °C | 0,011 m3/s |  | Dpmin = 24589 Pa |  |  | 8,50 turns |  |  | 22202-001100 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.7.2.2 |  | CARC-O-3-1 | TA-Modulator 1" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,00033 m3/s |  | Dpmin = 17914 Pa |  |  | pos. 5,9 |  |  | 52164-325 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 400000 Pa | Actuating time : 65,1 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.7.3.1 |  | AHU-O-4-1 | TA-Fusion-P 4" | Ductile iron |  | ANSI Flange | US specific |  | Press. rate250 psi-350 psi; -20/120 °C | 0,011 m3/s |  | Dpmin = 24927 Pa |  |  | 8,69 turns |  |  | 22202-001100 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.7.3.2 |  | CARC-O-4-1 | TA-Modulator 1" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,00033 m3/s |  | Dpmin = 17914 Pa |  |  | pos. 5,9 |  |  | 52164-325 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 400000 Pa | Actuating time : 65,1 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.8.1 |  | CARC-O-1-1 | TA-Modulator 1 1/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -20/120 °C | 0,00061 m3/s |  | Dpmin = 19677 Pa |  |  | pos. 5,1 |  |  | 52164-332 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 600000 Pa | Actuating time : 65,6 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.8.2 |  | AHU-O-1-1 | TA-Fusion-P 4" | Ductile iron |  | ANSI Flange | US specific |  | Press. rate250 psi-350 psi; -20/120 °C | 0,012 m3/s |  | Dpmin = 25265 Pa |  |  | 8,84 turns |  |  | 22202-001100 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | TA-Fusion-P 4"; ; US specific; ANSI Flange | 3
|  | - | TA-Fusion-P 5"; ; US specific; ANSI Flange | 1
|  | - | TA-Fusion-P 6"NF; ; US specific; ANSI Flange | 1
|  | - | Adapter 03; Adapter for TA-SLIDER 750/1250, TA-MC55(Y), TA-MC100(FSE/FSR) actuators | 5
|  | - | TA-Modulator 3"; ; US specific; Flange | 2
|  | - | TA-Slider 160 (1m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 19
|  | - | TA-Slider 500 (1m); Actuating force = 500 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 5
|  | - | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 7
|  | V006TCMN00 | TBV-CM 3/4"(20NF); Kvs = 2; Standard; NPT thread | 2
|  | V010TCMN00 | TBV-CM 1"(25NF); Kvs = 4; Standard; NPT thread | 11
|  | - | TA-Modulator 3/4"; ; US specific; Thread male | 1
|  | - | TA-Modulator 1"; ; US specific; Thread male | 3
|  | - | TA-Modulator 1 1/4"; ; US specific; Thread male | 2
|  | - | TA-Modulator 1 1/2"; ; US specific; Thread male | 3
|  | - | TA-Modulator 2"; ; US specific; Thread male | 2
|  | - | STAF-SG 2 1/2"; Standard; ANSI Flange; PN 300 psi | 1
|  | - | STAF-SG 3"; Standard; ANSI Flange; PN 300 psi | 2
|  | - | STAF-SG 4"; Standard; ANSI Flange; PN 300 psi | 4
|  | - | STAF-SG 8"; Standard; ANSI Flange; PN 300 psi | 3
|  | V020793CBV | STAP 2"; [20000-80000] Pa; Standard; NPT thread; PN 250 psi | 1
|  | V030794223 | STAP 3"; [40000-160000] Pa; Standard; ANSI Flange; PN 300 psi | 1
|  | - | STAD* 2"; Without drain; NPT thread; PN 350 psi | 1