## Valves export (1)
Technical informations | #1 | #2 | Primary product | [17 empty] | Secondary product | [21 empty] | Selection mode
|  |  | Product | [6 empty] | Technical informations | [7 empty] | Article N° | Victaulic Nr. | Qty | Product | [14 empty] | Technical informations |  |  |  | Article N° | Victaulic Nr. | Qty
|  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Flow | Power/DT | Dp | Dpl | Dpmin | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [9 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
| Boiler min. flow baypass |  | TA-Modulator 1 1/2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0016 m3/s |  | Dpmin = 23800 Pa |  |  | 1,87 turns |  |  | 52164-340 |  | 1 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | [9 empty] | 32222510111 |  | 1 | Individual selection
| OAHU-LB-2-1-Coil-1 |  | STAF-SG 2 1/2" |  | 2 1/2" (65) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,0033 m3/s |  | Dp=3000 Pa |  |  | 5,97 turns |  |  | 52182-965 |  | 1 | [22 empty] | Individual selection
| OAHU-LB-2-1-Coil-2 |  | STAF-SG 2 1/2" |  | 2 1/2" (65) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,0033 m3/s |  | Dp=3000 Pa |  |  | 5,97 turns |  |  | 52182-965 |  | 1 | [22 empty] | Individual selection
| B-1 |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,013 m3/s |  | Dp=5620 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| B-2 |  | STAF-SG 4" |  | 4" (100) | ANSI Flange | Standard |  | Press. rate300 psi; -20/120 °C | 0,013 m3/s |  | Dp=5620 Pa |  |  | 8,00* turns |  |  | 52182-990 |  | 1 | [22 empty] | Individual selection
| *A.1.1.1 | FCU-PH-2-2 | TA-Modulator 1 1/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -20/120 °C | 0,00047 m3/s |  | Dpmin = 19160 Pa |  |  | pos. 3,9 |  |  | 52164-332 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 600000 Pa | Actuating time : 65,6 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.1.2 | FCU-PH-2-1 | TA-Modulator 1 1/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -20/120 °C | 0,00047 m3/s |  | Dpmin = 19160 Pa |  |  | pos. 3,9 |  |  | 52164-332 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 600000 Pa | Actuating time : 65,6 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.1.3 | OAHU-LB-2-1 | TA-Modulator 2 1/2" | Ametal(tm) |  | Flange | US specific |  | Press. rate350 psi; -20/120 °C | 0,0066 m3/s |  | Dpmin = 27839 Pa |  |  | 4,95 turns |  |  | 322021-11003 |  | 1 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222610110 |  | 1 | Hydraulic Network
| *A.1.2 | H-L01-DPCV-1 | STAP 2 1/2" |  | 2 1/2" (65) | ANSI Flange | Standard | [20000-80000] Pa | Press. rate300 psi; -10/120 °C | 0,0034 m3/s |  |  | Dpl = 66823 Pa | 11412 Pa | 69,12 turns | Hmin = 81235 Pa |  |  | V024794116 | 1 | STAF-SG 2 1/2" | [10 empty] | 2 1/2" (65) | ANSI Flange | Standard | Press. rate300 psi; -20/120 °C | 0,0034 m3/s |  | Dp=3000 Pa | 6,20 turns | 52182-965 |  | 1 | Hydraulic Network
| *A.1.2.1 | LGS-04S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00033 m3/s |  | Dp = 52742 Pa |  |  | pos. 3,7 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.2 | LGS-04W-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00031 m3/s |  | Dp = 50497 Pa |  |  | pos. 8,2 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.3 | LGS-03S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00042 m3/s |  | Dp = 50916 Pa |  |  | pos. 5,0 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.4 | LGS-03W-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00035 m3/s |  | Dp = 46284 Pa |  |  | pos. 4,2 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.5 | LGS-02S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,0005 m3/s |  | Dp = 45975 Pa |  |  | pos. 6,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.6 | LGS-02W-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00031 m3/s |  | Dp = 41347 Pa |  |  | pos. 8,5 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.7 | LGS-01S-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00033 m3/s |  | Dp = 37689 Pa |  |  | pos. 9,2 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.8 | LGS-01W-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00031 m3/s |  | Dp = 35407 Pa |  |  | pos. 8,9 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.9 | LGS-SV-02 | TBV-CM 1/2"(15NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00011 m3/s |  | Dp = 35809 Pa |  |  | pos. 6,5 |  |  |  | V004TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.10 | FCU-LB-1-10 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00035 m3/s |  | Dp = 16706 Pa |  |  | pos. 7,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.2.11 | FCU-LB-1-11 | TBV-CM 1/2"(15NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 8,833e-5 m3/s |  | Dp = 31822 Pa |  |  | pos. 5,1 |  |  |  | V004TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3 | H-L01-DPCV-2 | STAP 2 1/2" |  | 2 1/2" (65) | ANSI Flange | Standard | [20000-80000] Pa | Press. rate300 psi; -10/120 °C | 0,0032 m3/s |  |  | Dpl = 48914 Pa | 10219 Pa | 46,46 turns | Hmin = 62133 Pa |  |  | V024794116 | 1 | STAF-SG 2 1/2" | [10 empty] | 2 1/2" (65) | ANSI Flange | Standard | Press. rate300 psi; -20/120 °C | 0,0032 m3/s |  | Dp=3000 Pa | 5,88 turns | 52182-965 |  | 1 | Hydraulic Network
| *A.1.3.1 | LGS-05W-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00031 m3/s |  | Dp = 33320 Pa |  |  | pos. 9,2 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.2 | LGS-05S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00033 m3/s |  | Dp = 31837 Pa |  |  | pos. 4,9 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.3 | LGS-06S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00045 m3/s |  | Dp = 30716 Pa |  |  | pos. 7,4 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.4 | LGS-06W-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00035 m3/s |  | Dp = 26988 Pa |  |  | pos. 5,7 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.5 | LGS-06S-02 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00045 m3/s |  | Dp = 28281 Pa |  |  | pos. 7,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.6 | LGS-07W-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00045 m3/s |  | Dp = 22878 Pa |  |  | pos. 8,3 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.7 | LGS-07S-01 | TBV-CM 1"(25NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,0005 m3/s |  | Dp = 20444 Pa |  |  | pos. 9,6 |  |  |  | V010TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 1,85e+6 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.8 | LGS-SV-01 | TBV-CM 1/2"(15NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00011 m3/s |  | Dp = 20843 Pa |  |  | pos. 9,0 |  |  |  | V004TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.9 | FCU-LB-1-1 | TBV-CM 1/2"(15NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 9,464e-5 m3/s |  | Dp = 20306 Pa |  |  | pos. 7,5 |  |  |  | V004TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.3.10 | LGS-WST-01 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00017 m3/s |  | Dp = 15001 Pa |  |  | pos. 8,2 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4 | H-L01-DPCV-3 | STAP 1 1/4" |  | 1 1/4" (32) | NPT thread | Standard | [20000-80000] Pa | Press. rate250 psi; -20/120 °C | 0,00084 m3/s |  |  | Dpl = 51631 Pa | 12418 Pa | 32,75 turns | Hmin = 68495 Pa |  |  | V012793CBV | 1 | STAD* 1 1/4" | [10 empty] | 1 1/4" (32) | NPT thread | Without drain | Press. rate350 psi; -20/120 °C | 0,00084 m3/s |  | Dp=4446 Pa | 4,00* turns | 52851-532 |  | 1 | Hydraulic Network
| *A.1.4.1 | FCU-LB-1-5 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00025 m3/s |  | Dp = 37999 Pa |  |  | pos. 7,9 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4.2 | FCU-LB-1-4 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,0002 m3/s |  | Dp = 32414 Pa |  |  | pos. 7,1 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4.3 | FCU-LB-1-3 | TBV-CM 1/2"(15NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00015 m3/s |  | Dp = 29144 Pa |  |  | pos. 10,0* |  |  |  | V004TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.4.4 | FCU-LB-1-2 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00023 m3/s |  | Dp = 21962 Pa |  |  | pos. 8,7 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.5 | H-L01-DPCV-4 | STAP 1 1/4" |  | 1 1/4" (32) | NPT thread | Standard | [20000-80000] Pa | Press. rate250 psi; -20/120 °C | 0,00087 m3/s |  |  | Dpl = 58789 Pa | 13369 Pa | 38,15 turns | Hmin = 76944 Pa |  |  | V012793CBV | 1 | STAD* 1 1/4" | [10 empty] | 1 1/4" (32) | NPT thread | Without drain | Press. rate350 psi; -20/120 °C | 0,00087 m3/s |  | Dp=4786 Pa | 4,00* turns | 52851-532 |  | 1 | Hydraulic Network
| *A.1.5.1 | FCU-LB-1-6 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00021 m3/s |  | Dp = 39845 Pa |  |  | pos. 6,8 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.5.2 | FCU-LB-1-7 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00016 m3/s |  | Dp = 31708 Pa |  |  | pos. 5,6 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.5.3 | FCU-LB-1-8 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,0003 m3/s |  | Dp = 29158 Pa |  |  | pos. 10,0* |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network
| *A.1.5.4 | FCU-LB-1-9 | TBV-CM 3/4"(20NF) | Ametal(tm) |  | NPT thread | Standard |  | Press. rate250 psi; -20/120 °C | 0,00019 m3/s |  | Dp = 23897 Pa |  |  | pos. 7,6 |  |  |  | V006TCMN00 | 1 | TA-Slider 160 (1m) | Close-off Dp : 660000 Pa | Actuating time : 40 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | Max. Temp. : 120°C | [8 empty] | 32222410111 |  | 1 | Hydraulic Network

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | TA-Modulator 2 1/2"; ; US specific; Flange | 1
|  | - | TA-Slider 160 (1m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 31
|  | - | TA-Slider 500 (1m); Actuating force = 500 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
|  | - | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
|  | V004TCMN00 | TBV-CM 1/2"(15NF); Kvs = 1; Standard; NPT thread | 5
|  | V006TCMN00 | TBV-CM 3/4"(20NF); Kvs = 2; Standard; NPT thread | 13
|  | V010TCMN00 | TBV-CM 1"(25NF); Kvs = 4; Standard; NPT thread | 11
|  | - | TA-Modulator 1 1/4"; ; US specific; Thread male | 2
|  | - | TA-Modulator 1 1/2"; ; US specific; Thread male | 1
|  | - | STAF-SG 2 1/2"; Standard; ANSI Flange; PN 300 psi | 4
|  | - | STAF-SG 4"; Standard; ANSI Flange; PN 300 psi | 2
|  | V012793CBV | STAP 1 1/4"; [20000-80000] Pa; Standard; NPT thread; PN 250 psi | 2
|  | V024794116 | STAP 2 1/2"; [20000-80000] Pa; Standard; ANSI Flange; PN 300 psi | 2
|  | - | STAD* 1 1/4"; Without drain; NPT thread; PN 350 psi | 2