## Valves export (1)
Technical informations | #1 |  | #2 | Primary product | [17 empty] | Secondary product | [20 empty] | Selection mode
|  |  |  | Product | [6 empty] | Technical informations | [7 empty] | Article N° | Victaulic Nr. | Qty | Product | [13 empty] | Technical informations |  |  |  | Article N° | Victaulic Nr. | Qty
|  |  |  | Name | Body Material | Size | Connection | Version | Dpl range | PN; Tmin/Tmax | Flow | Power/DT | Dp | Dpl | Dpmin | Setting | Hmin | Author. |  |  |  | Name | Actuator informations | [8 empty] | Size | Connection | Version | PN; Tmin/Tmax | Flow | Power/DT | Dp | Setting
|  |  |  | TA-Modulator 1 1/4" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -20/120 °C | 0,00092 m3/s |  | Dpmin = 22075 Pa |  |  | pos. 8,7 |  |  | 52164-332 |  | 1 | TA-Slider 160 (1m) | Close-off Dp : 600000 Pa | Actuating time : 65,6 s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | [8 empty] | 32222410111 |  | 1 | Individual selection
|  | Cv accessory |  | ACCXS_1 1/4"NPT ; Soldering NPT connection | [14 empty] | 52009-732 |  | 5
|  |  |  | TA-Modulator 1 1/2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0014 m3/s |  | Dpmin = 23846 Pa |  |  | 1,77 turns |  |  | 52164-340 |  | 2 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | [8 empty] | 32222510111 |  | 2 | Individual selection
|  | Cv accessory |  | Thermal insulation DN40 ; Thermal insulation (EPP for heating/comfort cooling) for TA-Modulator | [14 empty] | 52164-905 |  | 2
|  |  |  | TA-Modulator 2" | Ametal(tm) |  | Thread male | US specific |  | Press. rate250 psi; -10/90 °C | 0,0028 m3/s |  | Dpmin = 25460 Pa |  |  | 1,83 turns |  |  | 52164-350 |  | 2 | TA-Slider 500 (1m) | Close-off Dp : 400000 Pa | Actuating time : 150; 300* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | 0(2)-10 V | - | No relay | Fail Safe : No | Default return position : None | [8 empty] | 32222510111 |  | 2 | Individual selection
|  | Cv accessory |  | Thermal insulation DN50 ; Thermal insulation (EPP for heating/comfort cooling) for TA-Modulator | [14 empty] | 52164-906 |  | 9
|  |  |  | TA-Modulator 2 1/2" | Ametal(tm) |  | Flange | US specific |  | Press. rate350 psi; -20/120 °C | 0,0033 m3/s |  | Dpmin = 23983 Pa |  |  | 3,83 turns |  |  | 322021-11003 |  | 2 | TA-Slider 750 (24V) | Close-off Dp : 800000 Pa | Actuating time : 60; 80; 120; 160; 240; 320* s | IP auto(man.) : 54 | 24 VAC; 24 VDC | On-off; 3-point; 0(2)-10 V; 0(4)-20 mA | 0(2)-10 V | No relay | Fail Safe : No | Default return position : None | [8 empty] | 32222610110 |  | 2 | Individual selection
|  |  |  | STAD* 2" |  | 2" (50) | NPT thread | Without drain |  | Press. rate350 psi; -20/120 °C | 0,0014 m3/s |  | Dp=3000 Pa |  |  | 3,68 turns |  |  | 52851-550 |  | 3 | [21 empty] | Individual selection
|  | Bv accessory |  | Extension for measuring point M14x1 ; Extension for measuring point M14x1 | [14 empty] | 52179-016 |  | 6
|  |  |  | STAD* 1 1/4" |  | 1 1/4" (32) | NPT thread | Without drain |  | Press. rate350 psi; -20/120 °C | 0,00083 m3/s |  | Dp=4475 Pa |  |  | 4,00* turns |  |  | 52851-532 |  | 2 | [21 empty] | Individual selection
|  |  |  | STAD* 1/2" |  | 1/2" (15) | NPT thread | Without drain |  | Press. rate350 psi; -20/120 °C | 0,00014 m3/s |  | Dp=3824 Pa |  |  | 4,00* turns |  |  | 52851-515 |  | 1 | [21 empty] | Individual selection
|  | Bv accessory |  | Self-sealing measuring point extension ; Self-sealing measuring point extension | [14 empty] | 52179-006 |  | 9
|  |  |  | STAD* 1/2" |  | 1/2" (15) | NPT thread | Without drain |  | Press. rate350 psi; -20/120 °C | 3,333e-5 m3/s |  | Dp=3001 Pa |  |  | 2,14 turns |  |  | 52851-515 |  | 1 | [21 empty] | Individual selection
|  | Bv accessory |  | Extension for measuring point M14x1 ; Extension for measuring point M14x1 | [14 empty] | 52179-016 |  | 2
|  |  |  | STS* 20 |  | 3/4" (20) | Thread | With drain 3/4" |  | Press. rate350 psi; -20/120 °C | 4,167e-5 m3/s |  | 48,6 Pa | [5 empty] | 52849-620 |  | 1 | [21 empty] | Individual selection
|  | Sv accessory |  | Allen key (5mm) ; | [14 empty] | 58187-105 |  | 1
|  | Sv accessory |  | Measuring point (103mm) ; Measuring point (103mm) | [14 empty] | 52179-015 |  | 2
|  | Sv accessory |  | Self-sealing measuring point extension ; Self-sealing measuring point extension | [14 empty] | 52179-006 |  | 8
|  | Sv accessory |  | Transition nipple G3/4 ; Transition nipple G3/4 | [14 empty] | 52179-986 |  | 7

## Pneumatex export (2)
Pressurisation and Water Quality selection | [7 empty] | Pressurisation input data | [18 empty] | Pressurisation calculated data | [17 empty] | Separator tech. info |  |  |  | Safety valve tech. info | [6 empty] | Product parameters
| #1 | #2 | Qty | Product name | Product function | Article N° | Victaulic Nr. |  | Application type | Fluid type: | Norm | Water content [Vs] | Installed power [Qs] | Static height [Hst] | Min. required equipment pressure [pz] | Safety valve response pressure [pSV] | Safety temperature limiter [TAZ] | Maximum temperature [tsmax] | Supply temperature | Return temperature | Minimum temperature [tsmin] | Fill temperature | Pressurisation on | Pump head | Max width | Max height | Expansion coefficient [e] | Expansion volume [Ve] | Min. water reserve [Vwr,min] | Water reserve [Vwr] | Contracted volume [Vcontr] | Vapour over-pressure [pv] | Minimum pressure [p0] | Min. initial pressure [pa,min] | Initial pressure [pa] | Filling pressure [pfill] | Target pressure [pman] | Final pressure [pe] | Specific flowrate of equalization volume [qN/Q] | Necessary flowrate of equalization volume [qN] | Pressure factor [PF] | Required nominal volume | Expansion pipe up to (10 m) [DNe] | Expansion pipe up to (30 m) [DNe] |  | Flow | Power/DT | Dp |  | Set pressure | Heat generator type | Power 100% | Power | Max. collector | Collector
[9 empty] | - | - | - | m3 | W | m | Pa | Pa | °C | °C | °C | °C | °C | °C | - | Pa | m | m | - | m3 | m3 | m3 | m3 | Pa | Pa | Pa | Pa | Pa | Pa | Pa | m3/s/W | m3/s | - | m3 | - | - |  | m3/s | W/°C | Pa |  | Pa | - | W | W | m2 | m2
Pressurisation
Individual selection
[9 empty] | Heating | Water | None | 5 m3 | 60000 W | 10 m | - | 300000 Pa | 100 °C |  | 80 °C | 75 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0290 | 0,145 m3 | 0,025 m3 | 0,043 m3 | 0,0015 m3 | 0 Pa | 118100 Pa | 148100 Pa | 138798 Pa | 139585 Pa | - | 250000 Pa | - | - | 2,65 | 0,451 m3 | - | -
|  |  | 2 | SU 500.3 | Statico | 710 1013 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,5 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 63 kg | Max. weight = 563 kg
|  |  | 3 | DLV 20 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 746 2000
|  |  | 2 | DD 18.10 | Intermediate vessel | 714 2022 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,018 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 6,3 kg | Max. weight = 24,3 kg
[9 empty] | Heating | Water | None | 5 m3 | 60000 W | 10 m | - | 300000 Pa | 100 °C |  | 80 °C | 75 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0290 | 0,145 m3 | 0,025 m3 | 0,079 m3 | 0,0015 m3 | 0 Pa | 118100 Pa | 148100 Pa | 152150 Pa | 152881 Pa | - | 250000 Pa | - | - | 2,65 | 0,457 m3 | - | -
|  |  | 3 | SU 200.3 | Statico | 710 1010 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,2 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 30 kg | Max. weight = 230 kg
|  |  | 5 | DLV 20 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 746 2000
|  |  | 3 | DD 8.10 | Intermediate vessel | 714 2020 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3,9 kg | Max. weight = 11,9 kg
|  |  | 1 | V 4.1 E Connect | TecBox - Vento Degassing | 812 1101 | [50 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 1 | Refill 36000 | Pleno Refill Softening | 813 3220 | [50 empty] | Capacity = 6,42 m3/mol/m3 | Heigth = 0,38 m | Weight = 6,2 kg
[9 empty] | Heating | Water | EN 12828 | 5 m3 | 60000 W | 10 m | - | 300000 Pa | 100 °C |  | 80 °C | 75 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0290 | 0,145 m3 | 0,025 m3 | 0,079 m3 | 0,0015 m3 | 0 Pa | 118100 Pa | 148100 Pa | 152150 Pa | 152881 Pa | - | 250000 Pa | - | - | 2,65 | 0,457 m3 | - | -
|  |  | 2 | SU 600.3 | Statico | 710 1014 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,6 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 70 kg | Max. weight = 670 kg
|  |  | 2 | DLV 20 A | Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 746 2000
|  |  | 2 | DD 18.10 | Intermediate vessel | 714 2022 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,018 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 6,3 kg | Max. weight = 24,3 kg
|  |  | 2 | V 4.1 E Connect | TecBox - Vento Degassing | 812 1101 | [50 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 2 | P AB5 R | TecBox - Pleno Make-up water | 813 3330 | [50 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
|  |  | 2 | Refill 36000 | Pleno Refill Softening | 813 3220 | [50 empty] | Capacity = 6,42 m3/mol/m3 | Heigth = 0,38 m | Weight = 6,2 kg
[9 empty] | Heating | Water | EN 12828 | 5 m3 | 60000 W | 10 m | - | 300000 Pa | 100 °C |  | 80 °C | 75 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0290 | 0,145 m3 | 0,025 m3 |  | 0,0015 m3 | 0 Pa | 118100 Pa | 148100 Pa |  | 120675 Pa | 168100 Pa | 188100 Pa | 1,5500e-10 m3/s/W | 9,3e-6 m3/s | 1,10 | 0,189 m3 | 1 1/4" (32) | 1 1/2" (40)
|  |  | 3 | TV 4.1 EH | TecBox - Transfero | 811 1510 | [50 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 3 | SD 50.10 | Buffer vessel | 710 3005 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,05 m3 | PS = 1e+6 Pa | Temp. range = 5/70 °C | Weight = 12 kg | Max. weight = 62 kg
|  |  | 3 | Manometer H | Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 501 1037
|  |  | 3 | TU 300 | Primary vessel | 713 1001 | [50 empty] | Connection = Thread ISO228 Female RP | Nom. volume = 0,3 m3 | PS = 200000 Pa | Temp. range = 5/70 °C | Weight = 44 kg | Max. weight = 344 kg
|  |  | 9 | DD 8.10 | Intermediate vessel | 714 2020 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3,9 kg | Max. weight = 11,9 kg
|  |  | 3 | P BA4 R | TecBox - Pleno Make-up water | 813 3310 | [50 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
|  |  | 3 | Refill 48000 | Pleno Refill Softening | 813 3230 | [50 empty] | Capacity = 8,56 m3/mol/m3 | Heigth = 0,38 m | Weight = 6,2 kg
[9 empty] | Cooling | Water/Methyl Alcohol - 0% by weight | None | 5 m3 | 60000 W | 10 m | - | 300000 Pa |  | 20 °C | 6 °C | 12 °C | 1 °C | 15 °C | pump suction | - | 0 m | 0 m | 0,00159 | 0,008 m3 | 0,025 m3 |  | 0,0033 m3 | 0 Pa | 118079 Pa | 148079 Pa |  | 127545 Pa | 158079 Pa | 168079 Pa | 1,0667e-10 m3/s/W | 6,4e-6 m3/s | 1,10 | 0,036 m3 | 3/4" (20) | 3/4" (20)
|  |  | 1 | Simply Compresso C 2.1-80 S | TecBox - Compresso Compressor | 301021 41001 | [50 empty] | PS = 375000 Pa | Power = 300 W | Supply voltage = 230 VAC
|  |  | 1 | CD 80.9 | Integrated vessel | - | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,08 m3 | PS = 900000 Pa | Temp. range = 5/70 °C | Weight = 16 kg | Max. weight = 96 kg
|  |  | 1 | DD 8.10 | Intermediate vessel | 714 2020 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,008 m3 | PS = 1e+6 Pa | Temp. range = -10/110 °C | Weight = 3,9 kg | Max. weight = 11,9 kg
|  |  | 15 | P | TecBox - Pleno Make-up water | *** ****(deleted) | [50 empty] | PS = 1e+6 Pa | Power = 20 W | Supply voltage = 230 VAC
|  |  | 2 | V 4.1 E Connect | TecBox - Vento Degassing | 812 1101 | [50 empty] | PS = 1e+6 Pa | Power = 750 W | Supply voltage = 230 VAC
|  |  | 2 | P BA4 R | TecBox - Pleno Make-up water | 813 3310 | [50 empty] | PS = 1e+6 Pa | Power = 0 W | Supply voltage = -
|  |  | 2 | Refill 36000 | Pleno Refill Softening | 813 3220 | [50 empty] | Capacity = 6,42 m3/mol/m3 | Heigth = 0,38 m | Weight = 6,2 kg
[9 empty] | Solar | Water |  | 0,166 m3 | 0 W | 0 m | - | 300000 Pa | 100 °C |  | 70 °C | 50 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0228 | 0,0038 m3 | 0,003 m3 | 0,029 m3 | 4,981e-5 m3 | 0 Pa | 20000 Pa | 50000 Pa | 186682 Pa | 187366 Pa | - | 250000 Pa | - | - | 1,52 | 0,037 m3 | - | -
|  |  | 100 | SD 50.3 | Statico | 710 1005 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,05 m3 | PS = 300000 Pa | Temp. range = 5/70 °C | Weight = 8 kg | Max. weight = 58 kg
|  |  | 100 | Thermometer/Manometer TH | Pressure display range 0-4 bar, temperature display range 0-120 °C, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Rear connection. | 501 1038
[9 empty] | Solar | Water |  | 0,166 m3 | 0 W | 0 m | - | 300000 Pa | 100 °C |  | 70 °C | 50 °C | 5 °C | 10 °C | pump suction | - | 0 m | 0 m | 0,0228 | 0,0038 m3 | 0,003 m3 | 0,047 m3 | 4,981e-5 m3 | 0 Pa | 20000 Pa | 50000 Pa | 207546 Pa | 208038 Pa | - | 250000 Pa | - | - | 1,52 | 0,04 m3 | - | -
|  |  | 3 | MN-80 | Membrane vessel | 11111 015080 | [50 empty] | Connection = Thread ISO228 Male R | Nom. volume = 0,08 m3 | PS = 600000 Pa | Temp. range = -10/100 °C | Weight = 12,4 kg | Max. weight = 92,4 kg
|  |  | 3 | PI | TecBox - Pleno Make-up water | *** ****(deleted) | [50 empty] | PS = 1e+6 Pa | Power = 40 W | Supply voltage = 230 VAC
|  |  | 3 | Refill 6000 Filter | Pleno Refill Softening | 813 3010 | [50 empty] | Capacity = 1,07 m3/mol/m3 | Heigth = 0,571 m | Weight = 4,1 kg
|  |  | 12 | Electronic water meter | Electronic water meter with countdown function for manual make up. | 813 3121
|  |  | 3 | Filter cartridge | Spare filter cartridge | 813 3111
Safety valves
Individual selection
[10 empty] | Hot water(-10 / 120 °C) | [39 empty] | 200000 Pa | Heating, Direct | 68000 W | 60000 W
|  |  | 2 | DSV 15-2.0 DGH | - | 536 1020 | [50 empty] | Size = 1/2" (15) | Connection (in / out ) = Thread (G 1/2" / G 1")
[10 empty] | Hot water(-10 / 120 °C) | [39 empty] | 250000 Pa | Heating, Direct | 277000 W | 600000 W
|  |  | 3 | DSV 25-2.5 DGH | - | 536 3025 | [50 empty] | Size = 1" (25) | Connection (in / out ) = Thread (G 1" / G 1 1/2")
|  |  | 3 | ET 65-250 | Blow tank | 785 2501 | [50 empty] | Size = DN2 1/2"/5"/3/4" | PS = 200000 Pa

## Article list (3)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | P; PN 150 psi | 15
|  | - | MN-80; Standard; PN 125 psi | 3
|  | - | PI; PN 150 psi | 3
|  | - | Refill 6000 Filter; With filter; PN 125 psi | 3
|  | - | Simply Compresso C 2.1-80 S | 1
|  | - | CD 80.9; Standard; PN 125 psi | 1
|  | - | DD 8.10; Standard; PN 150 psi | 1
|  | - | TA-Modulator 2 1/2"; ; US specific; Flange | 2
|  | - | TA-Slider 160 (1m); Actuating force = 160 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
|  | - | TA-Slider 500 (1m); Actuating force = 500 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 4
|  | - | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 2
|  | - | ACCXS_1 1/4"NPT; Soldering NPT connection | 5
|  | - | TA-Modulator 1 1/4"; ; US specific; Thread male | 1
|  | - | TA-Modulator 1 1/2"; ; US specific; Thread male | 2
|  | - | TA-Modulator 2"; ; US specific; Thread male | 2
|  | - | Thermal insulation DN40; Thermal insulation (EPP for heating/comfort cooling) for TA-Modulator | 2
|  | - | Thermal insulation DN50; Thermal insulation (EPP for heating/comfort cooling) for TA-Modulator | 9
|  | - | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 17
|  | - | Measuring point (103mm); Length of 103mm and maximum temperature 120°C (intermittent 150°C). | 2
|  | - | Extension for measuring point M14x1; Length 71 mm. Suitable when insulation is used. | 8
|  | - | Transition nipple G3/4; For capillary pipe with G1/16 connection or for connection to TA valves with drain. | 7
|  | - | STS* 20; With drain 3/4"; Thread; PN 350 psi | 1
|  | - | STAD* 1/2"; Without drain; NPT thread; PN 350 psi | 2
|  | - | STAD* 1 1/4"; Without drain; NPT thread; PN 350 psi | 2
|  | - | STAD* 2"; Without drain; NPT thread; PN 350 psi | 3
|  | - | DSV 15-2.0 DGH; Diaphragm; Thread; PN 350 psi | 2
|  | - | DSV 25-2.5 DGH; Diaphragm; Thread; PN 350 psi | 3
|  | - | Allen key (5mm); | 1
|  | - | SD 50.3; Standard | 100
|  | - | Thermometer/Manometer TH; Pressure display range 0-4 bar, temperature display range 0-120 °C, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Rear connection. | 100
|  | - | SU 200.3; Standard | 3
|  | - | DLV 20 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 5
|  | - | DD 8.10; Standard; PN 150 psi | 3
|  | - | V 4.1 E Connect; PN 150 psi | 1
|  | - | Refill 36000; Standard; PN 125 psi | 1
|  | - | SU 500.3; Standard | 2
|  | - | DLV 20 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 3
|  | - | DD 18.10; Standard; PN 150 psi | 2
|  | - | SU 600.3; Standard | 2
|  | - | DLV 20 A; Connection set DLV A, female thread on both sides, 90° bend with threaded seal for direct connection to Statico SU expansion vessels. | 2
|  | - | DD 18.10; Standard; PN 150 psi | 2
|  | - | V 4.1 E Connect; PN 150 psi | 2
|  | - | P AB5 R; PN 150 psi | 2
|  | - | Refill 36000; Standard; PN 125 psi | 2
|  | - | ET 65-250; Vertical | 3
|  | - | TV 4.1 EH; PN 150 psi | 3
|  | - | TU 300; Standard | 3
|  | - | SD 50.10; Standard; PN 150 psi | 3
|  | - | Manometer H; Display range 0-4 bar, with 3 adjustable plastic segments for the marking of the desired green pressure bandwith. Bottom connection. | 3
|  | - | DD 8.10; Standard; PN 150 psi | 9
|  | - | P BA4 R; PN 150 psi | 3
|  | - | Refill 48000; Standard; PN 125 psi | 3
|  | - | V 4.1 E Connect; PN 150 psi | 2
|  | - | P BA4 R; PN 150 psi | 2
|  | - | Refill 36000; Standard; PN 125 psi | 2
|  | - | Filter cartridge; Spare filter cartridge | 3
|  | - | Electronic water meter; Electronic water meter with countdown function for manual make up. | 12