## Control products (1)
Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection) | Balancing and control valves / Actuators (from individual selection)
|  | Water Temperature: 6 °C | TA-FUSION-C 1 1/2" | 0,0014 m3/s |  | 22106-003040 | ** Generic Steel Pipes ** | 1
|  |  | Ametal(tm) | 10000 Pa |  |  | 1 1/2" (40)
|  |  | NPT thread | 9,19 turns |  |  | 1,02 m/s
|  |  | Standard |  |  |  | 331 Pa/m
Press. rate 250 psi; -20/120 °C
|  |  | TA-MC 100/24 |  |  | 61100-001 |  | 1
Close-off Dp : 800000 Pa
Actuating time : 240; 180*; 80; 38 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output Signal : 0-10 V
Relay type : No relay
Fail Safe : No
Default return position : None
Max. Temp. : -
ACA71 |  |  | Position switch unit (2 switches) |  |  | 67071-100 |  | 1
ACA72 |  |  | Enclosure protection IP 65 |  |  | 67072-100 |  | 1
|  | Water Temperature: 6 °C | TBV-CM 1"(25NF) | 0,0014 m3/s |  | V010TCMN00 | ** Generic Steel Pipes ** | 1
|  |  | Ametal(tm) | 158757 Pa |  |  | 1 1/2" (40)
|  |  | NPT thread | pos. 10,0* |  |  | 1,02 m/s
|  |  | Standard |  |  |  | 331 Pa/m
Press. rate 250 psi; -20/120 °C
|  |  | TA-ACTM 24/NC |  |  | ACTM30042001B |  | 1
Close-off Dp : 962500 Pa
Actuating time : 8,89 s
IP auto(man.) : 20
Power Supply : 24 VAC
Input : 0-10 V
Output Signal : -
Relay type : No relay
Fail Safe : Yes
Default return position : Extending
Max. Temp. : 90,0°C
|  | Water Temperature: 6 °C | TA-FUSION-C 1 1/4" | 0,0014 m3/s |  | 22106-003032 | ** Generic Steel Pipes ** | 1
|  |  | Ametal(tm) | 15264 Pa |  |  | 1 1/2" (40)
|  |  | NPT thread | 10,00* turns |  |  | 1,02 m/s
|  |  | Standard |  |  |  | 331 Pa/m
Press. rate 250 psi; -20/120 °C
|  |  | TA-MC 100FSE/24 |  |  | 61100-101 |  | 1
Close-off Dp : 800000 Pa
Actuating time : 40 s
IP auto(man.) : 54
Power Supply : 24 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output Signal : 0(2)-10 V; 0(4)-20 mA
Relay type : No relay
Fail Safe : Yes
Default return position : Extending
Max. Temp. : -

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | TA-FUSION-C 1 1/4"; Kvs = 12,9; Standard; NPT thread | 1
|  | - | TA-FUSION-C 1 1/2"; Kvs = 18,5; Standard; NPT thread | 1
|  | V010TCMN00 | TBV-CM 1"(25NF); Kvs = 4; Standard; NPT thread | 1
|  | - | TA-MC 100/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 1
|  | - | TA-MC 100FSE/24; Actuating force = 1000 N; Power Supply = 24 VAC; Relay type = No relay | 1
|  | - | ACA71; Position switch unit (2 switches) | 1
|  | - | ACA72; Enclosure protection IP 65 | 1
|  | - | TA-ACTM 24/NC; Actuating force = 125 N; Power Supply = 24 VAC; Relay type = No relay | 1