## Balancing valves (1)
Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves | Selected balancing valves
#1 | #2 | Water | Product | Technical Info | Radiator Info | Article N° | Pipe | Qty |  |  | §
Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection) | Balancing valves (from individual selection)
|  | Water Temperature: 6 °C | STAD* 1 1/2" | 0,0014 m3/s |  | 52867-540 | ** Generic Steel Pipes ** | 1
|  |  | 1 1/2" (40) | 6836 Pa |  |  | 1 1/2" (40)
|  |  | NPT thread | 4,00* turns |  |  | 1,02 m/s
|  |  | Without drain |  |  |  | 331 Pa/m
Press. rate 350 psi; -20/120 °C
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  | Water Temperature: 6 °C | STAD-B* 40 | 0,0014 m3/s |  | 52751-640 | ** Generic Steel Pipes ** | 1
|  |  | 1 1/2" (40) | 6287 Pa |  |  | 1 1/2" (40)
|  |  | Thread | 4,00* turns |  |  | 1,02 m/s
|  |  | With drain 3/4" |  |  |  | 331 Pa/m
Press. rate 350 psi; -20/120 °C
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
|  | Water Temperature: 6 °C | STA* 40 | 0,0014 m3/s |  | 52850-240 | ** Generic Steel Pipes ** | 1
|  |  | 1 1/2" (40) | 6836 Pa |  |  | 1 1/2" (40)
|  |  | Thread | 4,00* turns |  |  | 1,02 m/s
|  |  | With drain 1/2" |  |  |  | 331 Pa/m
Press. rate 350 psi; -20/120 °C
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  | Water Temperature: 6 °C | TA-BVS 143 DN40 | 0,0014 m3/s |  | 6-52143-040 | ** Generic Steel Pipes ** | 1
|  |  | 1 1/2" (40) | 4986 Pa |  |  | 1 1/2" (40)
|  |  | Flange | pos. 9,0* |  |  | 1,02 m/s
|  |  | FPM o-rings |  |  |  | 331 Pa/m
Press. rate 550 psi; -30/200 °C

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 4
|  | - | Extension for measuring point M14x1; Length 71 mm. Suitable when insulation is used. | 4
|  | - | STAD-B* 40; With drain 3/4"; Thread; PN 350 psi | 1
|  | - | STA* 40; With drain 1/2"; Thread; PN 350 psi | 1
|  | - | STAD* 1 1/2"; Without drain; NPT thread; PN 350 psi | 1
|  | - | TA-BVS 143 DN40; FPM o-rings; Flange; PN 550 psi | 1