## Control products (1)
Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products | Selected control products
#1 | #2 | Water | Product | Technical Info |  | Article N° | Pipe | Qty |  |  | §
Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection) | Control valves / Actuators (from individual selection)
|  | Water Temperature: 6 °C | CV 216 RGA 1 1/4" | 0,0014 m3/s |  | 60237-132 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 12,5 | 16257 Pa |  |  | 1 1/2" (40)
|  |  | Bronze | - |  |  | 1,02 m/s
|  |  | NPT thread |  |  |  | 331 Pa/m
Standard
Press. rate 250 psi; -15/150 °C
ACV 11 |  |  | Internal thread connect. parts of bronze |  |  | 68011-032 |  | 1
ACV 12 |  |  | Plug made of CrNi steel 1.4305 |  |  | 68012-032 |  | 1
ACV 13 |  |  | Stem heater |  |  | 68013-015 |  | 1
ACV 15 |  |  | Sealing FKM |  |  | 68015-032 |  | 1
ACV 16 |  |  | Technical silicon free version |  |  | 68016-032 |  | 1
|  |  | TA-MC 100/115 |  |  | 61100-302 |  | 1
Close-off Dp : 900000 Pa
Actuating time : 168; 126*; 56; 26,6 s
IP auto(man.) : 54
Power Supply : 115 VAC
Input : 3-point; 0(2)-10 V; 0(4)-20 mA
Output Signal : 0-10 V
Relay type : No relay
Fail Safe : No
Default return position : None
Max. Temp. : -
ACA71 |  |  | Position switch unit (2 switches) |  |  | 67071-100 |  | 1
ACA72 |  |  | Enclosure protection IP 65 |  |  | 67072-100 |  | 1
|  | Water Temperature: 6 °C | CV 216 RGA 3/4" | 0,0014 m3/s |  | 60237-220 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 6,3 | 63999 Pa |  |  | 1 1/2" (40)
|  |  | Bronze | - |  |  | 1,02 m/s
|  |  | NPT thread |  |  |  | 331 Pa/m
Standard
Press. rate 250 psi; -15/150 °C
|  |  | TA-Slider 750 Plus (24V) |  |  | 32222610219 |  | 1
Close-off Dp : 1,381e+6 Pa
Actuating time : 36; 48; 72; 96; 144; 192* s
IP auto(man.) : 54
Power Supply : 24 VAC; 24 VDC
Input : On-off; 3-point; 0(2)-10 V; 0(4)-20 mA
Output Signal : 0(2)-10 V; 0(4)-20 mA
Relay type : Relay 220V
Fail Safe : No
Default return position : None
Max. Temp. : 120°C
|  | Water Temperature: 6 °C | CV 316 RGA 1/2" | 0,0014 m3/s |  | 60337-515 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 4 | 158757 Pa |  |  | 1 1/2" (40)
|  |  | Bronze | - |  |  | 1,02 m/s
|  |  | NPT thread |  |  |  | 331 Pa/m
Standard
Press. rate 250 psi; -15/150 °C
ACV 11 |  |  | Internal thread connect. parts of bronze |  |  | 68011-015 |  | 1
ACV 13 |  |  | Stem heater |  |  | 68013-015 |  | 1
|  |  | TA-MC 55Y |  |  | 61055-003 |  | 1
Close-off Dp : 1,5e+6 Pa
Actuating time : 108; 60* s
IP auto(man.) : 54(30)
Power Supply : 24 VAC
Input : 0(2)-10 V; 0(4)-20 mA
Output Signal : 0-10 V
Relay type : No relay
Fail Safe : No
Default return position : None
Max. Temp. : -
|  | Water Temperature: 6 °C | CV 316 RGA 1" | 0,0014 m3/s |  | 60337-125 | ** Generic Steel Pipes ** | 1
|  |  | Kvs = 8 | 39689 Pa |  |  | 1 1/2" (40)
|  |  | Bronze | - |  |  | 1,02 m/s
|  |  | NPT thread |  |  |  | 331 Pa/m
Standard
Press. rate 250 psi; -15/150 °C
ACV 12 |  |  | Plug made of CrNi steel 1.4305 |  |  | 68012-025 |  | 1
|  |  | TA-Slider 750 (24V) |  |  | 32222610110 |  | 1
Close-off Dp : 1,031e+6 Pa
Actuating time : 42; 56; 84; 112; 168; 224* s
IP auto(man.) : 54
Power Supply : 24 VAC; 24 VDC
Input : On-off; 3-point; 0(2)-10 V; 0(4)-20 mA
Output Signal : 0(2)-10 V
Relay type : No relay
Fail Safe : No
Default return position : None
Max. Temp. : 120°C

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | TA-Slider 750 (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = No relay | 1
|  | - | TA-Slider 750 Plus (24V); Actuating force = 750 N; Power Supply = 24 VAC; 24 VDC; Relay type = Relay 220V | 1
|  | - | CV 216 RGA 1 1/4"; Kvs = 12,5; Standard; NPT thread | 1
|  | - | CV 216 RGA 3/4"; Kvs = 6,3; Standard; NPT thread | 1
|  | - | CV 316 RGA 1"; Kvs = 8; Standard; NPT thread | 1
|  | - | CV 316 RGA 1/2"; Kvs = 4; Standard; NPT thread | 1
|  | - | TA-MC 55Y; Actuating force = 600 N; Power Supply = 24 VAC; Relay type = No relay | 1
|  | - | TA-MC 100/115; Actuating force = 1000 N; Power Supply = 115 VAC; Relay type = No relay | 1
|  | - | ACA71; Position switch unit (2 switches) | 1
|  | - | ACA72; Enclosure protection IP 65 | 1
|  | - | ACV 11; Internal thread connect. parts of bronze | 1
|  | - | ACV 11; Internal thread connect. parts of bronze | 1
|  | - | ACV 12; Plug made of CrNi steel 1.4305 | 1
|  | - | ACV 12; Plug made of CrNi steel 1.4305 | 1
|  | - | ACV 13; Stem heater | 2
|  | - | ACV 15; Sealing FKM | 1
|  | - | ACV 16; Technical silicon free version | 1