## Dp controllers (1)
Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets | Selected differential pressure control sets
#1 | #2 | Water | Product | Technical Info | Radiator Info | Article N° | Pipe | Qty |  |  | §
Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection) | Dp controllers (from individual selection)
|  | Water Temperature: 6 °C | DA 516 DN25/32 | 0,0014 m3/s |  | 52795-025 | ** Generic Steel Pipes ** | 1
|  |  | 1 1/4" (32) | Dpl unknown |  |  | 1 1/2" (40)
|  |  | ANSI Flange -> 1 1/4" (32) | Dpmin = 17640 Pa |  |  | 1,02 m/s
|  |  | PT 90 | Scheme A |  |  | 331 Pa/m
[5000-30000] Pa
Press. rate 350 psi; -10/120 °C
|  | Water Temperature: 6 °C | STAP 1 1/2" | 0,0014 m3/s |  | V014793CBV | ** Generic Steel Pipes ** | 1
|  |  | 1 1/2" (40) | Dpl unknown |  |  | 1 1/2" (40)
|  |  | NPT thread | Dpmin = 15504 Pa |  |  | 1,02 m/s
|  |  | Standard | Scheme C |  |  | 331 Pa/m
[20000-80000] Pa
Press. rate 250 psi; -20/120 °C
Draining kit 1/2" |  |  | Can be installed during system operation. |  |  | 52265-201 |  | 1
Measuring point, two-way with G1/16 side connection. |  |  | For connection of capillary pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. |  |  | 52179-200 |  | 1
|  |  | STAD* 1 1/2" | 0,0014 m3/s |  | 52867-540 |  | 1
|  |  | 1 1/2" (40) | 6836 Pa
|  |  | NPT thread | 4,00* turns
Without drain
Press. rate 350 psi; -20/120 °C
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
Self-sealing measuring point extension |  |  | Length 60 mm. Can be installed without draining of the system. |  |  | 52179-006 |  | 2
|  | Water Temperature: 6 °C | DA 516 DN25/32 | 0,0014 m3/s |  | 52795-125 | ** Generic Steel Pipes ** | 1
|  |  | 1" (25) | Dpl unknown |  |  | 1 1/2" (40)
|  |  | ANSI Flange -> 1" (25) | Dpmin = 17640 Pa |  |  | 1,02 m/s
|  |  | PT 90 | Scheme B |  |  | 331 Pa/m
[10000-60000] Pa
Press. rate 350 psi; -10/120 °C
Capillary pipe connection with shut-off DN20-DN50 |  |  | For replacement of existing measuring point on STAF/STAF-SG, DN 20 to 50. |  |  | 52265-209 |  | 1
Impulse pipe connection kit (1/2") |  |  | For connecting 6 mm copper impulse pipe to STAD with 1/2" drain. |  |  | 52762-006 |  | 1
Measuring point, two-way with 6mm copper pipe side connection. |  |  | For connection of 6mm impulse pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. |  |  | 52179-206 |  | 1
|  |  | STAD* 1 1/4" | 0,0014 m3/s |  | 52867-532 |  | 1
|  |  | 1 1/4" (32) | 12607 Pa
|  |  | NPT thread | 4,00* turns
Without drain
Press. rate 350 psi; -20/120 °C
Extension for measuring point M14x1 |  |  | Length 71 mm. Suitable when insulation is used. |  |  | 52179-016 |  | 2
Scheme A
(DA 516)
Scheme B
(DA 516)
Scheme C
(STAP)

## Article list (2)
Article list | Article list | Article list | Article list | Article list | Article list | Article list
|  | Victaulic Nr. | Description | Qty
|  | - | Conn. Piece: ANSI Flange, 1" (25) | 1
|  | - | Conn. Piece: ANSI Flange, 1 1/4" (32) | 1
|  | - | Conn. Piece: ANSI Flange, 1" (25) | 1
|  | - | Conn. Piece: ANSI Flange, 1 1/4" (32) | 1
|  | - | Self-sealing measuring point extension; Length 60 mm. Can be installed without draining of the system. | 2
|  | - | Extension for measuring point M14x1; Length 71 mm. Suitable when insulation is used. | 4
|  | - | Measuring point, two-way with G1/16 side connection.; For connection of capillary pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. | 1
|  | - | Measuring point, two-way with 6mm copper pipe side connection.; For connection of 6mm impulse pipe while permitting simultaneous use of IMI Hydronic Engineering balancing instrument. | 1
|  | - | Draining kit 1/2"; Can be installed during system operation. | 1
|  | - | Capillary pipe connection with shut-off DN20-DN50; For replacement of existing measuring point on STAF/STAF-SG, DN 20 to 50. | 1
|  | V014793CBV | STAP 1 1/2"; [20000-80000] Pa; Standard; NPT thread; PN 250 psi | 1
|  | - | Impulse pipe connection kit (1/2"); For connecting 6 mm copper impulse pipe to STAD with 1/2" drain. | 1
|  | - | DA 516 DN25/32; [5000-30000] Pa; PT 90; ANSI Flange; PN 350 psi | 1
|  | - | DA 516 DN25/32; [10000-60000] Pa; PT 90; ANSI Flange; PN 350 psi | 1
|  | - | STAD* 1 1/4"; Without drain; NPT thread; PN 350 psi | 1
|  | - | STAD* 1 1/2"; Without drain; NPT thread; PN 350 psi | 1